## Settings
| Station | [5 empty] | Required Dead Times: |  |  |  | 2010-10-27 |  | Turlough Hill | 5A |  | Direction Limits | [5 empty] | Dead Times
| Feeder | [11 empty] | Dunstown |  |  | Phase - Phase |  | Phase - Earth |  | Delta Ang |  | 0.6 | 1.0
[13 empty] | 7SA611 | FALSE |  | -22 | 120 | -22 | 118 | 8
Device Configuration | [10 empty] | Delta Angle: | 10 | 7SA612 | TRUE |  |  |  |  | t add on for Fwd E/F if 7SA611 | 0
| [0121] PTT mode | [11 empty] | 7SD522 | FALSE |  |  | Healthy V, Ph Flts | 60
[13 empty] | Type= | 7SA612 |  |  | Healthy V, E Flts | 63 | 120 | 63 | 120
Power System Data 1: |  |  |  |  | [0203] VT Pri. kV | 220 | Power System Data 2: |  | [1104] Full Scale | 500 |  |  | In= | 5 | 1 | RBB | TRUE
| [0201] CT Starpoint | Busbar | [0211]Match Ratio | 1.73 | [0204] VT Sec. V | 100 | [1116] RE/RL, Z1 | 0.93 | [1117] XE/XL, Z1 | 0.85 | [1133A] Line open |  | Op.Time | 30
[5 empty] | [0205] CT Pri. A | 1800 | [1118] RE/RL | 0.93 | [1119] XE/XL | 0.85 | before SOTF | 1.5 | Dir T4= | 1 | [6 empty] | Load encroachment
| CT Data (7SD522 only): |  | [0251] k_alf/k_alf nominal | 1.5 |  |  | [0253] CT Error at k_alf/k_alf nominal | 2% |  |  | [0254] CT Error at k_alf nominal | 10% | Starpoint= | 0 | 180 | I-DIFF> PU | 0.2 |  |  |  | 99999
General Settings: | [12 empty] | Gen. Trafo | FALSE | [6 empty] | 72
| [1202] Min. Iph> | 0.16 | [1211] Ang.of Inc | 75 | [1232] Man. Close |  |  |  | [1203] EFDet. Ie> | 0.16 | [1206] Delay 1ph-faults | 0.05
| [1241] R Load, (ph-e) | oo | [1242] Φ Load, (ph-e) | 60 | [1243] R Load, (ph-ph) | 72 | [1244] Φ Load, (ph-ph) | 60 |  |  |  |  | Address Changes | [5 empty] | 1 Inactive
Zone Settings: | [12 empty] | [13 | [12 | Teleprotection | 1 PUTT, (Z1B acceleration) |  | SOTF | 2 With Pickup (Non-directional)
| Zone 1 |  | Zone 1B |  | Zone 2 |  | Zone 3 |  | Zone 4 |  | Zone 5 |  |  |  |  | 2 PUTT, (acceleration with PU) |  |  | 3 With Zone Z1B
| [1301] Op Mode | Forward | [1351] Op Mode | Forward | [1311] Op Mode | Forward | [1321] Op Mode | Reverse | [1331] Op Mode | Forward | [1341] Op Mode | Reverse |  |  |  | 3 POTT |  |  | 4 Zone Z1B undirectional
| [1302] R(Z1) | 13.64 | [1352] R(Z1B) | 22.73 | [1312] R(Z2) | 17.05 | [1322] R(Z3) | 2.27 | [1332] R(Z4) | 34.09 | [1342] R(Z5) | 11.36 |  |  |  | 4 Disabled | 3 POTT |  | 4 Zone Z1B undirectional
| [1303] X(Z1) | 8.05 | [1353] X(Z1B) | 15.16 | [1313] X(Z2) | 12.16 | [1323] X(Z3) | 0.93 | [1333] X(Z4) | 22.9 | [1343] X(Z5)+ | 6.23 |  | Effective Min I> for EF | 0.16 |  |  | Test | Test
| [1304] RE(Z1) | 39.77 | [1354] RE(Z1B) | 79.55 | [1314] RE(Z2) | 62.5 | [1324] RE(Z3) | 4.55 | [1334] RE(Z4) | 90.91 | [1344] RE(Z5) | 28.41 |  |  | Zone Enabled |  |  | TRUE | TRUE | TRUE
| [1305 / 06] T1 | 0 | [1355 / 56] T1B | 0 | [1315 / 16] T2 | 0.4 | [1325] T3 | 0.4 | [1335] T4 | 0.9 | [1345] T5 | 1.1 | Effective X5: |  | CTStarPoint | Zone 1 | Zone 1B | Zone 2 | Zone 3 | Zone 4 | Zone 5
| [1307], Z Red.Ang | 0 | [8 empty] | [1346] X(Z5)- | 26.79 | 26.79 |  | 0 | 1 | 1 | 1 | 0 | 1 | 0
[15 empty] | Result => | 1 | 1 | 1 | 0 | 1 | 0
| Switch On To Fault: |  | Weak Infeed | [11 empty] | Dir. Selection |  |  | 1 | 0 | 1
| [2404] Isc | 2 | [2505] U/V (ph-e) | 35 | [10 empty] | Convert for CT Starpoint
[15 empty] | Starting | Dir.1 | Dir.1B | Dir.2 | Dir.3 | Dir.4 | Dir.5
Backup (Emergency) Overcurrent Settings: | [8 empty] | Sensitive E/Fault: |  | [3002] 3Uo> PU | 50 |  |  | 0 | 0 | 0 | 0 | 180 | 0 | 180
| [2610] Iph >> | 2.4 | [2611] T Iph >> | 0.1 | [2612] 3Io >> | 3.6 | [2613] T 3Io >> | oo | [3003] Uph-e min. | 40 | [3004] Uph-e max. | 75
| [2620] Iph > | 1.5 | [2621] T Iph > | 0.9 | [2622] 3Io > | 0.5 | [2623] T 3I0 > | 0.9 | [3005] 3Io> Rel. | 0.008 | [3006] Time [s] | 2.5
[15 empty] | Scheme: | Normal | Scheme | 0
Earth Fault OvercurrentSettings: | [10 empty] | AutoReclose | [6 empty] | 1
DCEF | [3131] 3Io > | 0.1 | [3164] Min 3Uo | 1.7 |  |  | [3303] Ie> | 0.01 |  |  |  |  | Inverse Time E/F |  | FALSE
| [3162A] Alpha | 338 | [3163A] Beta | 122 |  |  | [3304] Delay Time | 2 |  |  | [3457] D Time after 3pole . | 1 | Extremely Inverse | 80 | 2 |  |  | R | X
[13 empty] | Long Time Inverse | 120 | 1 |  |  | 76.7561 | 14.8925
CB Fail Settings: | [12 empty] | Normal Inverse | 0.14 | 0.02 |  |  | 153.5315 | 28.046 |  |  | Vn[V] | 100
| [3902] I > | 0.1 | [3905] T1, Retrip | 0.1 | [3906] T2, Busbar | 0.2 | [3907] T3, CB Def. | 0.04 |  |  |  |  | Very Inverse | 13.5 | 1 |  |  | 120.625 | 22.496 |  |  | DIFGI[A] | 0.05 | DIFIC[A] | 0.09
[13 empty] | Long Time Inverse | 120 | 1 |  |  | 8.7815 | 1.7205 |  |  | VT Ratio | 2200
Differential Settings: (7SD522 Only) | [12 empty] | I/Ie | A/Ph | Time |  |  | 175.4563 | 42.365
| [1210] I-DIFF> PU [A] | 1 | [1213] I-DIFF> SOTF | 1 | [1217A] I-DIFF>Trip time | 0 | [1218] Delay 1ph-flts | 0.05 | [1233] I-DIFF>> PU[A] | 6.8 | [1235] I-DIFF>> SOTF | 6.8 | 20 | 0.33333 | 1.2932 |  |  | 54.8313 | 49.5615 |  |  | Diff SOTF | OK
[13 empty] | 10 | 0.16667 | 2.6967 |  |  | 0
[13 empty] | 8 | 0.13333 | 3.4586
[13 empty] | 6 | 0.1 | 4.83 |  |  | Zone 2 | Zone 3 | Zone 4
[13 empty] | 4 | 0.066667 | 8.03 |  | R | 17.05 | 2.27 | 34.09
[13 empty] | 2 | 0.033333 | 24.03 |  | X | 12.16 | 0.93 | 22.9
[13 empty] | 1.5 | 0.025 | 48.03 |  | RE | 62.5 | 4.55 | 90.91
[13 empty] | 1 | 0.016667 |  |  | t | 0.4 | 0.4 | 0.9
[13 empty] | Back-Up OverCurrent | [6 empty] | 1-Ph Fault Model
[13 empty] | Ph Setting | FALSE | FALSE |  |  |  |  | 60 | 0 | 53.4 | 0
[13 empty] | EF Setting | FALSE | FALSE |  |  |  |  | 60 | -120 | 60 | -120 | TRUE | 178
[20 empty] | 60 | 120 | 60 | 120 | OK | OK
[20 empty] | 0 | 0 | 0.626 | 154
[13 empty] | SOTF Isc | TRUE | 2 |  |  |  |  | 0 | 0 | 0 | 0
[13 empty] | SOTF Test Voltage | [6 empty] | 0 | 0 | 0 | 0
[13 empty] | Ph-Ph | #REF!
[13 empty] | Ph-E | #REF! | [5 empty] | 2-Ph Fault Model |  |  | 43.3481
[20 empty] | 60 | 150 | 41.2543 | 133.3481
[13 empty] | Load Angle | 45 | [5 empty] | 60 | 30 | 41.2543 | 46.6519
[13 empty] | Basic Dir. | 1 |  | Display | Zph | Ze |  | 60 | 270 | 60 | 270
[13 empty] | Max Rch | #REF! |  | Max Reach | FALSE | FALSE |  | 0 | 0 | 1.309 | 317
[16 empty] | Load Encroachment | FALSE | FALSE |  | 0 | 0 | 1.309 | 137
[13 empty] | 1 |  |  | Z5 | TRUE | TRUE |  | 0 | 0 | 0 | 0
[13 empty] | 0 |  |  | Z4 | TRUE | TRUE |  |  |  | OK | OK
[13 empty] | 1 |  |  | Z3 | TRUE | TRUE |  | Evolving Fault Limits Warning |  |  | OK
[16 empty] | Flt Model | TRUE | TRUE |  | 3-Ph Fault Model |  |  | 0.139
[13 empty] | Resultant | 1 | [5 empty] | 60 | 0 | 32.7 | 0
[8 empty] | Model | 76.6997 | 37.4089 | [9 empty] | 60 | -120 | 32.7 | -120
[8 empty] | Locator | 0 | 0 | [9 empty] | 60 | 120 | 32.7 | 120
|  | Model | 31.6522 | 29.5162 | [15 empty] | 0 | 0 | 1.5115 | 137
|  | Locator | 196.3599 | 71.2674 | [15 empty] | 0 | 0 | 1.5115 | 17
[14 empty] | Ph Scaler | 85 |  |  |  |  | 0 | 0 | 1.5115 | 257
|  |  | 208.8929 | 19.948 |  |  |  |  | 200 | -16.1 |  |  |  | EF scaler | 81 |  |  |  |  | TRUE | 109 | OK | OK
Fault Locator
[6 empty] | Vr | 60 | 127.9 |  |  | DCEF:??? |  |  | 3Uo | -13.4897029941728+17.361803677193j |  |  | R-S |  | S-T |  | T-R
| Fault Model |  |  |  |  | Vs | 38.04 | 52.1 |  |  | Fault Model |  |  | Vr | -36.8571 | 47.345 | -36.8571120059366+47.3450450900814j | -60.2245210177004+17.3282865029698j |  | 23.3674090117638+90.0167585871116j |  | 36.8571120059366-107.345045090081j
| Impedance | 43.2789 |  |  |  | Vt | 60 | 270 |  |  | Impedance | 85.3362 |  | Vs | 23.3674 | 30.0168 | 23.3674090117638+30.0167585871116j | -0.485410196624968+0.352671151375484j |  | 0.242705098312484-0.176335575687742j |  | 0.242705098312484-0.176335575687742j
| Angle | 43 |  |  |  | Ir | 0.3 | 324 |  |  | Angle | 26 | Starpoint Correction | Vt | -1.1026e-14 | -60 | -1.10263360941776E-14-60j | 98.179953725592+35.6336783604697j |  | -113.35297383883+288.533686256404j |  | 309.712881290013-217.266329535464j
| Fault Voltage | 56.6364 |  |  |  | Is | 0.3 | 144 |  |  | Fault Voltage | 53.4 | 144 | Ir | -0.24271 | 0.17634 | -0.242705098312484+0.176335575687742j | 208.8929 | 19.948 | 620.0019 | 111.4478 | 756.6419 | -35.05
| Fault Current | 1.309 |  |  |  | It | 0 | 0 |  |  | Fault Current | 0.626 | 324 | Is | 0.24271 | -0.17634 | 0.242705098312484-0.176335575687742j | R-S | TRUE | S-T | FALSE | T-R | FALSE
[6 empty] | 3Uo | 21.9865 | 127.8463 |  |  | E/F loops | released | 180 | It | 0 | 0 | 0 | 196.3599 | 71.2674 | -226.7059 | 577.0674 | 619.4258 | -434.5327
[6 empty] | 3Io | 0 | 0 | [5 empty] | 3Io | 0 |  |  | Ph-Ph Selection | TRUE
|  |  | MW | 10 |  |  | E/F loops | blocked
|  |  | MVar | 10 | [13 empty] | R-E |  | S-E |  | T-E
[18 empty] | 192.155830831519-55.4629306604754j |  | 4.20407661966512+126.730287381415j |  | #NUM!
[18 empty] | 200 | -16.1 | 126.8 | 88.1 | #NUM! | #NUM!
[18 empty] | R-E | TRUE | S-E | FALSE | T-E | FALSE
[18 empty] | 192.1558 | -55.4629 | 4.2041 | 126.7303 | #NUM! | #NUM!
[18 empty] | E/F Selection | FALSE
Turlough Hill / Dunstown Settings Summary
7SA612, In = 5
2025-05-15
[0121] PTT mode: 3 POTT
CT: 1800/5, VT: 220kV/100V
[0201] CT Starpoint : Towards the Busbar
[1116] RE/RL, Z1 : 0.93, [1117] XE/XL, Z1 : 0.85
[1232] Man. Close : 4 Zone Z1B undirectional
[1302] R(Z1) : 13.64, [1303] X(Z1) : 8.05, [1304] RE(Z1) : 39.77
[1301] Op Mode : Forward; [1305 / 06] T1 : 0
[1312] R(Z2) : 17.05, [1313] X(Z2) : 12.16, [1314] RE(Z2) : 62.5
[1322] R(Z3) : 2.27, [1323] X(Z3) : 0.93, [1324] RE(Z3) : 4.55
[1352] R(Z1B) : 22.73, [1353] X(Z1B) : 15.16, [1354] RE(Z1B) : 79.55
[1203] EFDet. Ie>:0.16, [1202] Min. Iph>:0.16
[2404] SOTF Isc: 2
[2602] Em. O/C I>> : 2.4, [2603] tI>> : 0.1
[2612] Em. O/C I> : 1.5, [2613] tI> : 0.9
[2632] Em. O/C Ie>> : 3.6, [2633] tIe>> : oo
[2642] Em. O/C Ie> : 0.5, [2643] tIe> : 0.9
| 1-Ph Fault Model |  |  |  | Evolving Fault
| 60 | 0 | 53.4 | 0 | 41.2543 | 343.3481 | 32.7 | 0
| 60 | -120 | 60 | -120 | 41.2543 | 256.6519 | 32.7 | -120
| 60 | 120 | 60 | 120 | 60 | 120 | 32.7 | 120
| 0 | 0 | 0.626 | 154 | 1.309 | 167 | 1.5115 | 137
| 0 | 0 | 0 | 0 | 1.309 | 347 | 1.5115 | 17
| 0 | 0 | 0 | 0 | 0 | 210 | 1.5115 | 257
| 2-Ph Fault Model |  |  |  | 3-Ph Fault Model
| 60 | 150 | 41.2543 | 133.3481 | 60 | 0 | 32.7 | 0
| 60 | 30 | 41.2543 | 46.6519 | 60 | -120 | 32.7 | -120
| 60 | 270 | 60 | 270 | 60 | 120 | 32.7 | 120
| 0 | 0 | 1.309 | 317 | 0 | 0 | 1.5115 | 137
| 0 | 0 | 1.309 | 137 | 0 | 0 | 1.5115 | 17
| 0 | 0 | 0 | 0 | 0 | 0 | 1.5115 | 257
Note on L1: 07/02/08: Warnings if - [3002]<>50, [3003] <>40, [3004] <>75, [3162A]<>338, [3163A] <>122, [3164] <1.7 19/05/08: Generator Trafo Apps added 29/05/08: Cell reference for Z5 timing corrected (only impacts on 7SA611 where X3>>X5 only) "AR Dead Time" cross check against "Line open before SOTF [1133A] added (7SA611apps only) 26/06/08: Cell references corrected for timing test buttons 02/01/09: Min Rev V set to 1.5 when Zone 5 is only reverse zone (MOL very short reverse zone) 07/01/09: Min Forward Manual Timing Test voltage reduced to cater for extremly long Zone 4 compared to Zone 1 (50/1) 16/04/09: Voltage calculation for manual timing tests modified for arc-suppressed systems 7SD522 support added 22/09/09: EF Calcs Primary values added 27/10/09: Rounding of test currents changed for Timing macros 25/11/09: Test Voltages corrected for 7SA611 E/Fault timing tests Warning dialogue box added when E/F load-encroachment is not set to Infinity 02/03/10: Max Voltage for Reverse faults corrected Phase selection and clipboard support for E/Fault manual timing tests added 15/06/10: Warning messages added for Differential SOTF settings Differential 'Calibration' measurands message box enhanced 21/06/10: Voltage angles corrected for manual timing tests corrected (E/F loops only) GPS current angles corrected (7SD522, CT starpoint towards the line only) Quadrant 4 E/F directional limit and graphic plot corrected 29/06/10: Reverse healthy phase angles for arc-suppressed systems corrected. 13/07/10: Dead Times added to automate AR logic SSIMUL macros 10/10/10: Fault Models and Fault Locator added. 27/10/10: SOTF Min Voltage reduced to 2%
Note on R7: Scaler for nominal current: In 7SA61x, all settings are directly in Ohms, Amps etc. rather than multiples of In. Hence always equal to '1'
Note on M9: 7SA611 Defaults: 0.25 on Trafos, 1.5s on Lines Must be 500ms longer than AR Dead Time [3457]
Note on M12: 7SA611: Standard setting 0.05s
Note on J26: 7SA611 / 38kV applications only
Note on M26: Default = 50V. Confirm any changes with Setting provider
Note on D27: Enter 'oo' for Infinity
Note on H27: Enter 'oo' for Infinity
Note on K27: Default = 40V. Confirm any changes with Setting provider
Note on M27: Default = 75V. Confirm any changes with Setting provider
Note on D28: Enter 'oo' for Infinity
Note on H28: Enter 'oo' for Infinity
Note on L30: 7SA611 / 38kV applications only
Note on E31: Default setting of 1.7 should not be changed
Note on C32: Default Angles of 338 & 122 should not be changed.
Note on AA35: If VTs are NOT connected, DIFIC must be set to zero or If VTs are connected, appropriate setting should be applied to DIFIC
Note on E38: Networks Policy is to set I-Diff >SOTF equal to I-Diff >PU Check with Setting Provider if they are different. SOTF must not be set less than PU.
Note on M38: Networks Policy is to set I-Diff>> SOTF equal to I-Diff >>PU Check with Setting Provider if they are different. SOTF must not be set less than PU

## Characteristic
| Station: | Turlough Hill |  |  |  | Feeder: | Dunstown | [5 empty] | 7SA612 | [15 empty] | OK |  | Timing Delta Current | 3% |  |  | Z1 | Z1B | Z2 | Z3 | 29.6521 | Z5 | ZE1 | ZE1B | ZE2 | ZE3 | ZE4 | ZE5 |  | 1 | Fault detection | Z1 effective | Z1B Acceleration | Z1B Non Dir.
Phase to Phase Faults | [5 empty] | K Factor: | 1 | [21 empty] | Timing Warnings | OK | OK | Diff SOTF | OK | Corner Angle | 27.003 | 29.5028 | 30.912 | 200.2624 | 29.6521 | 235.3172 | 10.4499 | 9.8789 | 10.0718 | 190.545 | 12.7776 | 216.0417 |  | 2 | -14 | 0 | 0 | 0
[23 empty] | Ph-Ph Plot Data |  |  | Ph-E Plot Data |  |  | R-S | Faulty Ph1 | Faulty Ph2 | Healthy Ph | TRUE | Corner Mag | 35.4597 | 61.5676 | 47.3409 | 5.3707 | 92.5752 | 65.1575 | 82.1084 | 163.4702 | 128.6351 | 9.4013 | 191.5516 | 84.2347 |  | 3 | 0 | 17 | 20 | 20
|  | Z1, Forward |  |  | Z1B, Forward |  |  | Z2, Forward |  |  | Z3, Reverse |  | Z4, Forward |  | Z5, Reverse |  | PTT | POTT, Z1B | SOTF | 4 Zone Z1B undirectional |  |  | R | X |  | R | X |  | S-T | Healthy Ph | Faulty Ph1 | Faulty Ph2 | FALSE | b | 7.9773 | 15.177 | 12.1714 | 0.80883 | 22.9295 | 16.1542 | 0.60273 | 0.32449 | 0.15117 | 0.083522 | 8.5025 | 24.0723 |  | 4 | 20 | 37 | 40 | 40 |  |  |  | 1 |  |  | X
VA |  | 61.0339 | 330.5588 |  | 62.6498 | 208.6105 |  | 60 | 90 |  | 31.0629 | 254.9686 | 62.6498 | 331.3895 | 62.6498 | 208.6105 | 60 | 90 | 97.1019 | 342.0038 |  | Zone 1 | 25.5716 | -6.3757 | Zone 1 | 59.7306 | -14.8925 |  | T-R | Faulty Ph2 | Healthy Ph | Faulty Ph1 | FALSE | c | 26.0876 | 42.8517 | 31.8538 | 4.4674 | 64.2086 | 15.9763 | 76.7537 | 153.5312 | 120.6249 | 8.7811 | 175.2502 | 49.2645 |  | 5 | 40 | 90 | 90 | 90 | 25.5716 | -6.3757 | 59.7306 | -14.8925
VB |  | 61.0339 | 209.4412 |  | 60 | 90 |  | 62.6498 | 331.3895 |  | 60 | 90 | 62.6498 | 208.6105 | 60 | 90 | 62.6498 | 331.3895 | 97.1019 | 197.9962 |  | -35.0318 | 25.5716 | -6.3757 | -11.5666 | 72.7657 | -14.8925 |  | Test Voltages /Angles |  |  |  | R-S | d | 4.9853 | 10.432 | 8.8145 | 0.38168 | 15.8488 | 28.3411 | 0.16659 | 0.086212 | 0.040709 | 0.023233 | 2.7262 | 20.9565 |  | 6 | 90 | 143 | 140 | 140 | 25.5716 | -6.3757 | 72.7657 | -14.8925 | [5 empty] | d
VC |  | 60 | 90 |  | 62.6498 | 331.3895 |  | 62.6498 | 208.6105 |  | 31.0629 | 285.0314 | 60 | 90 | 62.6498 | 331.3895 | 62.6498 | 208.6105 | 60 | 90 |  | 0 | 27.28 | 0 | 0 | 76.7561 | 0 |  | Phase - Phase |  | Phase - Earth |  |  | Mag | 31.0729 | 53.2837 | 40.6683 | 4.8491 | 80.0575 | 44.3173 | 76.9203 | 153.6174 | 120.6656 | 8.8043 | 177.9764 | 70.2211 |  | 7 | 140.6755 | 163 | 160 | 160 | 27.28 | 0 | 76.7561 | 0
Current Limit: |  |  | 7.3A |  |  | 4A |  |  | 5A |  |  | 9.5A |  | 2.6A |  | 5.5A |  | 4A |  | 2.2A |  | 8.5 | 28.418 | 4.2471 | 4 | 78.2217 | 5.4698 |  | 60 | 60 | 60 | 63 |  | Corner 2Ang | -35.0318 | -39.0797 | -41.4022 | 155.2875 | -39.3245 | 98.8717 | -11.5666 | -10.8726 | -11.1062 | 168.3171 | -14.4753 | 129.9758 |  | 8 | 166 | 180 | 180 | 180 | 28.418 | 4.2471 | 78.2217 | 5.4698 |  |  |  | c | b
Pulse Duration (Cycles) |  |  | 5 |  |  | 5 |  |  | 25 |  |  | 25 |  | 50 |  | 60 |  | 5 |  | 5 |  | 17 | 29.7142 | 9.0845 | 8 | 79.7597 | 11.2095 |  | 0-180: | 180-360: | 60 | 60 |  | Corner 2 Mag | 28.0472 | 48.0964 | 36.7738 | 4.4491 | 72.2727 | 54.2288 | 74.274 | 148.6857 | 116.7844 | 8.4965 | 169.4849 | 64.675 |  | 9 | 180 | 197 | 200 | 200 | 29.7142 | 9.0845 | 79.7597 | 11.2095 | [5 empty] | Slope
ProTest Volts (Fault V) |  |  | 106.3039 |  |  | 110 |  |  | 110 |  |  | 16.1122 |  | 110 |  | 110 |  | 110 | 50 | 184.7028 |  | 26.958 | 31.5843 | 16.0638 | 10.4281 | 80.7376 | 14.859 |  | 61.3895 | 61.3895 | 60 | 60 |  | x | 10.0658 | 20.387 | 16.9245 | 0.827 | 30.9142 | 49.9652 | 3.1535 | 8.1117 | 5.8958 | 0.34352 | 1.4061 | 38.0371 |  | 10 | 233 | 217 | 220 | 220 | 31.5843 | 16.0638 | 80.7376 | 14.859 |  |  |  | a | R
Max. Reach @ Fault V |  |  | 664.3997 |  |  | 687.5 |  |  | 687.5 |  |  | 100.7015 |  | 687.5 |  | 687.5 |  | 687.5 |  | 1154.3927 |  | 37 | 21.3654 | 16.1 | 12 | 70.0637 | 14.8925 |  | Zone1 | Zone2 |  |  |  | y | 26.1788 | 43.5618 | 32.6477 | 4.3715 | 65.3272 | 21.077 | 74.207 | 148.4642 | 116.6355 | 8.4896 | 169.479 | 52.3071 |  | 11 | 237 | 270 | 270 | 270 | 21.3654 | 16.1 | 70.0637 | 14.8925
|  | Ang | Imp |  | Ang | Imp |  | Ang | Imp |  | Ang | Imp | Angle | Imped. | Angle | Imped. | Ang | Imp | Ang | Imp | I | 63.5 | 8.0272 | 16.1 | 51 | 12.0597 | 14.8925 |  | V | V |  |  |  | z | 0.1757 | 0.35586 | 0.29542 | 0.014435 | 0.53961 | 0.87215 | 0.055044 | 0.14159 | 0.10291 | 0.0059961 | 0.024543 | 0.66394 |  | 12 | 270 | 323 | 320 | 320 | 8.0272 | 16.1 | 12.0597 | 14.8925 |  |  |  | y | z
|  | -14 | 26.3545 |  | -14 | 43.9177 |  | -14 | 32.9431 |  | 166 | 4.386 | -14 | 65.8669 | 166 | 21.9492 | -14 | 43.9177 | -39.0797 | 92.3514 | 2 | 90 | 9.8624e-16 | 16.1 | 90 | 9.1228e-16 | 14.8925 |  | 60 | 60 |  |  |  | Blinder Mag | 26.3545 | 43.9177 | 32.9431 | 4.386 | 65.8669 | 21.9492 | 74.2621 | 148.6058 | 116.7384 | 8.4956 | 169.5036 | 52.971 |  | 13 | 278.8717 | 343 | 340 | 340 | 9.8624e-16 | 16.1 | 9.1228e-16 | 14.8925
|  | -35.0318 |  |  | -39.0797 |  |  | -41.4022 |  |  | 155.2875 |  | -39.3245 |  | 98.8717 |  | 0 | 45.46 | 0 | 92.3514 | 2 | 144.9682 | 9.8624e-16 | 16.1 | 168.4334 | 9.1228e-16 | 14.8925 |  | Deg. | Deg. | [17 empty] | 14 | 65.8669 | 27.28 | 45.46 | 45.46 | 9.8624e-16 | 16.1 | 9.1228e-16 | 14.8925 |  |  |  |  | x
|  | 0 | 27.28 |  | 0 | 45.46 |  | 0 | 34.1 |  | 180 | 4.54 | 0 | 68.18 | 180 | 22.72 | 10 | 48.4504 | 10 | 92.3514 | 2 | 112 | -6.5048 | 16.1 | 110 | -5.4204 | 14.8925 |  | 60.5588 | 61.3895 | [17 empty] | 15 | 68.18 | 31.0719 | 53.6054 | 53.6054 | -6.5048 | 16.1 | -5.4204 | 14.8925
|  | 8.5 | 28.7336 |  | 10 | 48.4504 |  | 10.5 | 36.493 |  | 189 | 4.8003 | 10 | 72.665 | 206.5 | 29.3019 | 20 | 53.6054 | 29.5028 | 92.3514 | 2 | Zone 1B | 42.6131 | -10.6246 | Zone 1B | 112.4864 | -28.046 |  | Zone3 | Zone1B |  |  |  | m | 5.1096 | 8.5148 | 6.387 | 0.85036 | 12.7703 | 4.2555 | 28.7533 | 57.5139 | 45.1869 | 3.2896 | 65.7271 | 20.5402 |  | 16 | 80.3963 | 26.7524 | 47.1695 | 47.1695 | 42.6131 | -10.6246 | #REF! | #REF!
|  | 17 | 31.0719 |  | 20 | 53.6054 |  | 21 | 40.7137 |  | 198 | 5.2289 | 20 | 80.3963 | 233 | 58.5837 | 29.5028 | 61.5676 | 65 | 92.3514 | 2 | -39.0797 | 42.6131 | -10.6246 | -10.8726 | 146.0166 | -28.046 |  | V | V |  |  |  | n | 12.6468 | 21.0749 | 15.8085 | 2.1047 | 31.6077 | 10.5328 | 71.167 | 142.3519 | 111.8416 | 8.1421 | 162.6802 | 50.8387 |  | 17 | 71.2522 | 16.1 | 30.32 | 30.32 | 42.6131 | -10.6246 | #REF! | #REF!
|  | 26.958 | 35.4346 |  | 29.5028 | 61.5676 |  | 30.912 | 47.3409 |  | 200.2624 | 5.3707 | 29.6521 | 92.5752 | 235.3172 | 65.1575 | 40 | 47.1695 | 90 | 92.3514 | 2 | 0 | 45.46 | 0 | 0 | 153.5315 | 0 |  | 60 | 60 |  |  |  | o | 16.7829 | 27.9673 | 20.9786 | 2.793 | 41.9448 | 13.9775 | 94.4418 | 188.9074 | 148.4188 | 10.8049 | 215.884 | 67.4652 |  | 18 | 45.8 | 26.7524 | 47.1695 | 47.1695 | 45.46 | 0 | #REF! | #REF!
|  | 37 | 26.7524 |  | 40 | 47.1695 |  | 41 | 37.0698 |  | 202 | 4.9652 | 40 | 71.2522 | 237 | 63.8868 | 65 | 33.4544 | 112 | 92.3514 | 2 | 10 | 47.7143 | 8.4133 | 4 | 156.4631 | 10.941 |  | Deg. | Deg. |  |  |  | Mag | 21.8925 | 36.4821 | 27.3656 | 3.6434 | 54.7152 | 18.233 | 123.1952 | 246.4213 | 193.6057 | 14.0945 | 281.6111 | 88.0054 |  | 19 |  | 31.0719 | 53.6054 | 53.6054 | 47.7143 | 8.4133 | #REF! | #REF! | x | 38.0371
|  | 63.5 | 17.9901 |  | 65 | 33.4544 |  | 65.5 | 26.7264 |  | 236 | 2.2436 | 65 | 50.5347 | 253.5 | 55.8812 | 90 | 30.32 | 140.9203 | 92.3514 | 2 | 20 | 50.3726 | 18.3341 | 8 | 159.5394 | 22.4218 |  | 15.0314 | 61.3895 | [17 empty] | 20 | 21.9492 | 27.28 | 45.46 | 45.46 | 50.3726 | 18.3341 | #REF! | #REF! | y | 52.3071
|  | 90 | 16.1 |  | 90 | 30.32 |  | 90 | 24.32 |  | 270 | 1.86 | 90 | 45.8 | 270 | 53.58 | 112 | 32.7012 | 180 | 92.3514 | 2 | 29.5028 | 53.5842 | 30.32 | 9.8789 | 161.0464 | 28.046 |  |  | Z4 |  | Z5 |  | Z1 |  | Z1B |  | Z2 |  | Z3 |  | Fwd Timing |  | PTT |  | SOTF |  | 21 | 22.72 | 31.0719 | 53.6054 | 53.6054 | 53.5842 | 30.32 | #REF! | #REF! | z | 0.66394
|  | 144.9682 |  |  | 140.9203 |  |  | 138.5978 |  |  | 335.2875 |  | 140.6755 |  | 278.8717 | 54.2288 |  |  | 209.5028 | 92.3514 | 2 | 40 | 36.134 | 30.32 | 12 | 131.9461 | 28.046 |  | Faulty Ph1 | 62.6498 | 331.3895 | 62.6498 | 331.3895 | 61.0339 | 330.5588 | 62.6498 | 331.3895 | 62.6498 | 331.3895 | 31.0629 | 285.0314 | 30.4993 | 100.3815 | 62.6498 | 331.3895 | 97.1019 | 342.0038 | 22 | 58.5837 | 26.7524 | 47.1695 | 47.1695 | 36.134 | 30.32 | #REF! | #REF! |  | 52.971
|  | 112 | 17.3644 |  | 112 | 32.7012 |  | 112 | 26.23 |  | 292 | 2.0061 | 112 | 49.3969 | 292 | 36.4661 |  |  | 270 | 92.3514 | 2 | 65 | 14.1384 | 30.32 | 51 | 22.7112 | 28.046 |  | Faulty Ph2 | 62.6498 | 208.6105 | 62.6498 | 208.6105 | 61.0339 | 209.4412 | 62.6498 | 208.6105 | 62.6498 | 208.6105 | 31.0629 | 254.9686 | 30.4993 | 79.6185 | 62.6498 | 208.6105 | 97.1019 | 197.9962 | 23 | 63.8868 | 16.1 | 30.32 | 30.32 | 14.1384 | 30.32 | #REF! | #REF!
[19 empty] | 292 | 92.3514 | 2 | 90 | 1.8573e-15 | 30.32 | 90 | 1.718e-15 | 28.046 |  | Healthy Ph | 60 | 90 | 60 | 90 | 60 | 90 | 60 | 90 | 60 | 90 | 60 | 90 | 60 | 270 | 60 | 90 | 60 | 90 | 24 | 53.58 | 26.7524 | 47.1695 | 47.1695 | 1.8573e-15 | 30.32 | #REF! | #REF!
Phase to Earth Faults | [5 empty] | K Factor: | 1 | [14 empty] | 140.9203 | 1.8573e-15 | 30.32 | 169.1274 | 1.718e-15 | 28.046 |  | Selection | R-S |  | T-R |  | R-S |  | T-R |  | S-T |  | T-R |  | R-S |  | S-T |  | R-S |  | 25 | 54.2288 | 31.0719 | 53.6054 | 53.6054 | 1.8573e-15 | 30.32 | #REF! | #REF!
|  | Z1, Forward |  |  | Z1B, Forward |  |  | Z2, Forward |  |  | Z3, Reverse |  | Z4, Forward |  | Z5, Reverse |  | PTT | POTT, Z1B | SOTF | 4 Zone Z1B undirectional |  | 112 | -12.2501 | 30.32 | 110 | -10.2079 | 28.046 |  | No Overreach |  | No Overreach | [16 empty] | 26 | -14 | 0 | 0 | 0 | -12.2501 | 30.32 | #REF! | #REF!
Faulty Phase R, S, T |  |  | 15.76V, 0º |  |  | 31.39V, 0º |  |  | 24.7V, 0º |  |  | 1.81V, 0º |  | 36.78V, 0º |  | 63V, 0º |  | 31.39V, 0º |  | 54.18V, 0º |  | Zone 2 | 31.9645 | -7.9697 | Zone 2 | 90.2265 | -22.496 |  | Z1B Released |  |  |  |  | Man Cl: | 4 Zone Z1B undirectional |  | B | PTT mode: | 3 POTT |  | A | PTT Tx | Z1B | GoNoGo Dir | NOOP |  |  | 27 | 0 | 8 | 8 | 8 | 31.9645 | -7.9697 | #REF! | #REF!
Healthy Phase S, T, R |  |  | 60V, 240º |  |  | 60V, 240º |  |  | 60V, 240º |  |  | 60V, 240º |  | 60V, 240º |  | 63V, 240º |  | 60V, 240º |  | 60V, 240º |  | -41.4022 | 31.9645 | -7.9697 | -11.1062 | 114.5972 | -22.496 |  |  | SOTF |  | Teleprotection |  | Z1B. | Z1B NonDir | FD |  |  | PTT Tx | Z1B E. | Z1B E NonDir | FD E |  |  | PTT E Tx |  |  | 28 | 11 | 12 | 12 | 12 | 31.9645 | -7.9697 | #REF! | #REF!
Healthy Phase T, R, S |  |  | 60V, 120º |  |  | 60V, 120º |  |  | 60V, 120º |  |  | 60V, 120º |  | 60V, 120º |  | 63V, 120º |  | 60V, 120º |  | 60V, 120º |  | 0 | 34.1 | 0 | 0 | 120.625 | 0 |  |  | Ph-Ph | Ph-E | Ph-Ph | Ph-E | A | B | C | D | E | F | A | B | C | D | E | F |  |  | 29 | 15 | 90 | 90 | 90 | 34.1 | 0 | #REF! | #REF!
Current Limit: |  |  | 1.2A |  |  | 1.2A |  |  | 1.2A |  |  | 1.2A |  | 1A |  | 1.4A |  | 1.2A |  | 2.1A |  | 10.5 | 35.8819 | 6.6503 | 4 | 122.9283 | 8.596 |  |  | -39.0797 | -10.8726 | -14 | -14 | -14 | -39.0797 | -14 |  |  | PTT_Tx V | -14 | -10.8726 | -14 |  |  | PTTe_Tx V |  |  | 30 | 90 | 168 | 168 | 168 | 35.8819 | 6.6503 | #REF! | #REF!
Pulse Duration (Cycles) |  |  | 5 |  |  | 5 |  |  | 25 |  |  | 25 |  | 50 |  | 60 |  | 5 |  | 5 |  | 21 | 38.0095 | 14.5905 | 8 | 125.3452 | 17.6161 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 110 | 0 | 0 | 0 |  |  | 31.3863 |  |  | 31 | #REF! | 172 | 172 | 172 | 38.0095 | 14.5905 | #REF! | #REF!
ProTest Volts (Fault V) |  |  | 15.762 |  |  | 31.3863 |  |  | 24.6979 |  |  | 1.805 |  | 36.7779 |  | 63 |  | 31.3863 | 43 | 54.18 |  | 30.912 | 40.6165 | 24.32 | 10.0718 | 126.6528 | 22.496 |  |  | 10 | 8 | 10 | 4 | 10 | 10 | 10 |  |  | I Limit | 4 | 8 | 11 |  |  | I Limit |  |  | 32 | 166 | 180 | 180 | 180 | 40.6165 | 24.32 | #REF! | #REF!
Max. Reach @ Fault V |  |  | 98.5122 |  |  | 196.1643 |  |  | 154.3622 |  |  | 11.2815 |  | 229.8619 |  | 393.75 |  | 196.1643 |  | 338.625 |  | 41 | 27.977 | 24.32 | 12 | 105.8354 | 22.496 |  |  | 29.5028 | 9.8789 | 20 | 8 | 20 | 29.5028 | 29.6521 |  |  | 4 | 8 | 9.8789 | 12.7776 |  |  | 1.2 |  |  | 33 | 180 | 188 | 188 | 188 | 27.977 | 24.32 | #REF! | #REF!
|  | Ang | Imp |  | Ang | Imp |  | Ang | Imp |  | Ang | Imp | Angle | Imped. | Angle | Imped. | Ang | Imp | Ang | Imp | I | 65.5 | 11.0833 | 24.32 | 51 | 18.2169 | 22.496 |  |  | 65 | 12 | 29.5028 | 9.8789 | 29.5028 | 65 | 65 |  |  | -14 | 9.8789 | 12 | 15 |  |  | -14 |  |  | 34 | 214 | 192 | 192 | 192 | 11.0833 | 24.32 | #REF! | #REF!
|  | -14 | 61.5591 |  | -14 | 115.93 |  | -14 | 92.9887 |  | 166 | 7.1118 | -14 | 169.5036 | 166 | 52.971 | -14 | 115.93 | -10.8726 | 148.6857 | 0.36439 | 90 | 1.4898e-15 | 24.32 | 90 | 1.378e-15 | 22.496 |  |  | 90 | 90 | 40 | 12 | 40 | 90 | 90 |  |  | 0 | 12 | 90 | 90 |  |  | 0 |  |  | 35 | 218 | 270 | 270 | 270 | 1.4898e-15 | 24.32 | #REF! | #REF!
|  | -11.5666 | 74.274 |  | -10.8726 | 148.6857 |  | -11.1062 | 116.7844 |  | 168.3171 | 8.4965 | -14.4753 |  | 129.9758 |  | 0 | 153.5315 | 0 | 153.5315 | 0.35289 | 138.5978 | 1.4898e-15 | 24.32 | 168.8938 | 1.378e-15 | 22.496 |  |  | 112 | 110 | 65 | 51 | 65 | 112 | 112 |  |  | 10 | 51 | 110 | 110 |  |  | 4 |  |  | 36 | 270 | 348 | 348 | 348 | 1.4898e-15 | 24.32 | #REF! | #REF!
|  | 0 | 76.7561 |  | 0 | 153.5315 |  | 0 | 120.625 |  | 180 | 8.7815 | 0 | 175.4563 | 180 | 54.8313 | 4 | 156.8452 | 8 | 161.1073 | 0.3363 | 112 | -9.8259 | 24.32 | 110 | -8.1879 | 22.496 |  |  | 140.9203 | 169.1274 | 90 | 90 | 90 | 140.9203 | 166 |  |  | 20 | 90 | 169.1274 | 166 |  |  | 8 |  |  | 37 | #REF! | 352 | 352 | 352 | -9.8259 | 24.32 | #REF! | #REF!
|  | 4 | 78.4127 |  | 4 | 156.8452 |  | 4 | 123.2285 |  | 184.5 | 8.9984 | 5.5 | 180.9361 | 197 | 62.4528 | 8 | 161.1073 | 9.8789 | 163.4702 | 0.33144 | Zone 3 | -4.2557 | 1.0611 | Zone 3 | -6.9005 | 1.7205 |  |  | 180 | 180 | 112 | 110 | 112 | 180 | 180 |  |  | 29.5028 | 110 | 180 | 180 |  |  | 9.8789 |  |  | 38 | 169.5036 | 76.7561 | 153.5315 | 153.5315 | -4.2557 | 1.0611 | #REF! | #REF!
|  | 8 | 80.5435 |  | 8 | 161.1073 |  | 8 | 126.5771 |  | 189 | 9.285 | 11 | 188.5613 | 214 | 80.729 | 9.8789 | 163.4702 | 12 | 134.8938 | 0.40165 | 155.2875 | -4.2557 | 1.0611 | 168.3171 | -8.3205 | 1.7205 |  |  | 209.5028 | 189.8789 | 0 | 0 |  | 209.5028 | 235.3172 |  |  | 40 |  | 189.8789 | 216.0417 |  |  | 12 |  |  | 39 | 175.4563 | 80.5435 | 161.1073 | 161.1073 | -4.2557 | 1.0611 | #REF! | #REF!
|  | 10.4281 | 82.0935 |  | 9.8789 | 163.4702 |  | 10.0718 | 128.6351 |  | 190.545 | 9.4013 | 12.7776 | 191.5516 | 216.0417 | 84.2347 | 12 | 134.8938 | 90 | 28.046 | 1.9318 | 180 | -4.54 | 5.5622e-16 | 180 | -8.7815 | 1.0759e-15 |  |  | 270 | 270 | 0 | 0 |  | 270 | 270 |  |  | 65 |  | 270 | 270 |  |  | 51 |  |  | 40 | 188.5613 | 71.629 | 134.8938 | 134.8938 | -4.54 | 5.5622e-16 | #REF! | #REF!
|  | 12 | 71.629 |  | 12 | 134.8938 |  | 12 | 108.1998 |  | 193 | 7.6483 | 15 | 163.6858 | 218 | 80.5012 | 51 | 36.0885 | 110 | 29.8459 | 1.8153 | 189 | -4.7412 | -0.75093 | 184.5 | -8.9707 | -0.70601 |  |  | 292 | 290 | 0 | 0 |  | 292 | 292 |  |  | 90 |  | 290 | 290 |  |  | 90 |  |  | 41 | 163.6858 | 14.8925 | 28.046 | 28.046 | -4.7412 | -0.75093 | #REF! | #REF!
|  | 51 | 19.1631 |  | 51 | 36.0885 |  | 51 | 28.9469 |  | 231.5 | 2.1984 | 52.5 | 53.3999 | 244 | 55.1422 | 90 | 28.046 | 169.1274 | 148.6857 | 0.36439 | 198 | -4.973 | -1.6158 | 189 | -9.1707 | -1.4525 |  |  | 48.0964 | 148.6857 | 43.9177 | 115.93 | 43.9177 | 48.0964 | 65.8669 |  |  | 112 | 115.93 | 148.6857 | 169.5036 |  |  | 110 |  |  | 42 | 42.365 | 71.629 | 134.8938 | 134.8938 | -4.973 | -1.6158 | #REF! | #REF!
|  | 90 | 14.8925 |  | 90 | 28.046 |  | 90 | 22.496 |  | 270 | 1.7205 | 90 | 42.365 | 270 | 49.5615 | 110 | 29.8459 | 180 | 153.5315 | 0.35289 | 200.2624 | -5.0384 | -1.86 | 190.545 | -9.2425 | -1.7205 |  |  | 45.46 | 153.5315 | 45.46 | 153.5315 | 45.46 | 45.46 | 68.18 |  |  |  | 153.5315 | 153.5315 | 175.4563 | [5 empty] | 43 | #REF! | 80.5435 | 161.1073 | 161.1073 | -5.0384 | -1.86 | #REF! | #REF!
|  | 168.4334 |  |  | 169.1274 |  |  | 168.8938 |  |  | 348.3171 |  | 165.5247 |  | 309.9758 |  |  |  | 189.8789 | 163.4702 | 0.33144 | 202 | -4.6037 | -1.86 | 193 | -7.4523 | -1.7205 |  |  | 48.4504 | 161.1073 | 48.4504 | 156.8452 | 48.4504 | 48.4504 | 72.665 |  |  | 43.9177 | 156.8452 | 161.1073 | 188.5613 |  |  | 115.93 |  |  | 44 | 52.971 | 76.7561 | 153.5315 | 153.5315 | -4.6037 | -1.86 | #REF! | #REF!
|  | 110 | 15.8483 |  | 110 | 29.8459 |  | 110 | 23.9397 |  | 290 | 1.8309 | 110 | 45.0839 | 290 | 52.7422 |  |  | 270 | 28.046 | 1.9318 | 236 | -1.2546 | -1.86 | 231.5 | -1.3685 | -1.7205 |  |  | 61.5676 | 163.4702 | 53.6054 | 161.1073 | 53.6054 | 61.5676 | 92.5752 |  |  | 45.46 | 161.1073 | 163.4702 | 191.5516 |  |  | 153.5315 |  |  | 45 | 54.8313 | 80.5435 | 161.1073 | 161.1073 | -1.2546 | -1.86 | #REF! | #REF!
[19 empty] | 290 | 29.8459 | 1.8153 | 270 | -3.4182e-16 | -1.86 | 270 | -3.1618e-16 | -1.7205 |  |  | 33.4544 | 134.8938 | 61.5676 | 163.4702 | 61.5676 | 33.4544 | 50.5347 |  |  | 48.4504 | 163.4702 | 134.8938 | 163.6858 |  |  | 156.8452 |  |  | 46 | 80.729 | 71.629 | 134.8938 | 134.8938 | -3.4182e-16 | -1.86 | #REF! | #REF!
Timing Tests | [21 empty] | 335.2875 | -3.4182e-16 | -1.86 | 348.3171 | -3.1618e-16 | -1.7205 |  |  | 30.32 | 28.046 | 47.1695 | 134.8938 | 47.1695 | 30.32 | 45.8 |  |  | 53.6054 | 134.8938 | 28.046 | 42.365 |  |  | 161.1073 |  |  | 47 | 80.5012 | 14.8925 | 28.046 | 28.046 | -3.4182e-16 | -1.86 | #REF! | #REF!
[22 empty] | 292 | 0.75149 | -1.86 | 290 | 0.62621 | -1.7205 |  |  | 32.7012 | 29.8459 | 33.4544 | 36.0885 | 33.4544 | 32.7012 | 49.3969 |  |  | 61.5676 | 36.0885 | 29.8459 | 45.0839 |  |  | 163.4702 |  |  | 48 | 49.5615 | 71.629 | 134.8938 | 134.8938 | 0.75149 | -1.86 | #REF! | #REF!
|  |  | Note: Zone 1B over-reaches Zone 2 ! | [18 empty] | Zone 4 | 63.9103 | -15.9346 | Zone 4 | 164.4686 | -41.0066 |  |  | 48.0964 | 148.6857 | 30.32 | 28.046 | 30.32 | 48.0964 | 21.9492 |  |  | 47.1695 | 28.046 | 148.6857 | 52.971 |  |  | 134.8938 |  |  | 49 | #REF! | 80.5435 | 161.1073 | 161.1073 | 63.9103 | -15.9346 | #REF! | #REF!
| Forward, [A] 90º |  |  | Time |  |  | Test Current Phase-Angle | [7 empty] | Inverse Time E/F | [6 empty] | -39.3245 | 63.9103 | -15.9346 | -14.4753 | 164.4686 | -41.0066 |  |  | 45.46 | 153.5315 | 32.7012 | 29.8459 | 32.7012 | 45.46 | 22.72 |  |  | 33.4544 | 29.8459 | 153.5315 | 54.8313 |  |  | 36.0885 | [7 empty] | 63.9103 | -15.9346 | #REF! | #REF!
|  |  |  | [ms] |  |  |  | Forward: |  | 90 | º |  |  |  | Angle | 0 | [5 empty] | 0 | 68.18 | 0 | 0 | 175.4563 | 0 |  |  | 61.5676 | 163.4702 | 0 | 0 |  | 61.5676 | 65.1575 |  |  | 30.32 |  | 163.4702 | 84.2347 |  |  | 28.046 | [7 empty] | 68.18 | 0 | #REF! | #REF!
| Zone 1, | 1.7068 | 1.7068 | 30 |  |  |  | Reverse: |  | 270 | º |  |  |  | A / Ph | Time [s] | [5 empty] | 10 | 71.561 | 12.6181 | 5.5 | 180.1031 | 17.342 |  |  | 30.32 | 28.046 | 0 | 0 |  | 30.32 | 53.58 |  |  | 32.7012 |  | 28.046 | 49.5615 |  |  | 29.8459 | [7 empty] | 71.561 | 12.6181 | #REF! | #REF!
| t1 | 0.70321 | 0.70321 | 30 | [17 empty] | 20 | 75.5478 | 27.4972 | 11 | 185.0969 | 35.9792 |  |  | Ph-Ph: 32.7012; Ph-E: 29.8459; Ph-Ph: 0; Ph-E: 0; B: 32.7012; C: 36.4661; B: 29.8459; C: 52.7422 | [7 empty] | 75.5478 | 27.4972 | #REF! | #REF!
| Zone 1B, | [5 empty] | Ph-Ph Fault Voltages | [14 empty] | 29.6521 | 80.4521 | 45.8 | 12.7776 | 186.808 | 42.365 | 7SA511 AR Logic | [24 empty] | 80.4521 | 45.8 | #REF! | #REF!
| t1B | [20 empty] | 40 | 54.5823 | 45.8 | 15 | 158.1083 | 42.365 | Z1B Untestable | FALSE | Ph-Ph: Ph-Ph SOTF; Ph-E: OK | [7 empty] | 54.5823 | 45.8 | #REF! | #REF!
| Zone 2, | 0.66225 | 0.66225 | 430 | [17 empty] | 65 | 21.3569 | 45.8 | 52.5 | 32.5078 | 42.365 | Z1/Z1b Timers |  | Ph-Ph: P-E SOTF; Ph-E: OK | [7 empty] | 21.3569 | 45.8 | #REF! | #REF!
| t2 | 0.46553 | 0.46553 | 430 |  |  | VA | 30.4993 | 100.3815 |  | 30.6813 | 102.0966 | [9 empty] | 90 | 2.8056e-15 | 45.8 | 90 | 2.5952e-15 | 42.365 | Disp.Z1B | No | [23 empty] | 2.8056e-15 | 45.8 | #REF! | #REF!
| Zone 3, | [5 empty] | VB | 30.4993 | 79.6185 |  | 30.6813 | 77.9034 | [9 empty] | 140.6755 | 2.8056e-15 | 45.8 | 165.5247 | 2.5952e-15 | 42.365 | Zone 2 | Forward | Ph-Ph: #REF!; E: -14; B: #REF!; C: #REF!; D: #REF!; E: #REF! | [7 empty] | 2.8056e-15 | 45.8 | #REF! | #REF!
| t3 | [5 empty] | VC | 60 | 270 |  | 60 | 270 | [9 empty] | 112 | -18.5044 | 45.8 | 110 | -15.4196 | 42.365 | Disp.Z2 | Yes | Ph-Ph: #REF!; E: #DIV/0!; B: #REF!; C: #REF!; D: #REF!; E: #REF! | [7 empty] | -18.5044 | 45.8 | #REF! | #REF!
| Zone 4 | 0.43802 | 0.43802 | 930 | [17 empty] | Zone 5 | -21.2972 | 5.31 | Zone 5 | -51.3976 | 12.8149 | 1 | 0 | Ph-Ph: #REF!; E: 27.09; B: #REF!; C: #REF!; D: #REF!; E: #REF! | [7 empty] | -21.2972 | 5.31 | #REF! | #REF!
| t4 | 0.2472 | 0.2472 | 930 |  |  | Phase-Earth Voltages | [14 empty] | 98.8717 | -21.2972 | 5.31 | 129.9758 | -51.3976 | 12.8149 | Disp.Z3 | Reverse | Ph-Ph: #REF!; E: 27.09; B: #REF!; C: #REF!; D: #REF!; E: #REF! | [7 empty] | -21.2972 | 5.31 | #REF! | #REF!
| No Op | 0.23259 | 0.23259 | [18 empty] | 180 | -22.72 | 2.7835e-15 | 180 | -54.8313 | 6.7176e-15 | Disp.Z4 | Forward | Ph-Ph: #REF!; A: Inverse Time E/F; E: 27.09; B: #REF!; C: #REF!; D: #REF!; E: #REF! | [7 empty] | -22.72 | 2.7835e-15 | #REF! | #REF!
| Fault Voltage | 10.992 | 10.17 | [18 empty] | 206.5 | -26.2233 | -13.0744 | 197 | -59.7239 | -18.2594 |  |  | Ph-Ph: #REF!; B: Formatting Info; E: 27.09; B: #REF!; C: #REF!; D: #REF!; E: #REF! | [7 empty] | -26.2233 | -13.0744 | #REF! | #REF!
[7 empty] | VA | 10.17 | 0 |  | 9.5158 | 0 | [9 empty] | 233 | -35.2565 | -46.787 | 214 | -66.9273 | -45.1431 | Rounding Fwd Ph/Ph | 3 | Ph-Ph: #REF!; B: 350; E: 51; B: #REF!; C: #REF!; D: #REF!; E: #REF! | [7 empty] | -35.2565 | -46.787 | #REF! | #REF!
| Reverse, [A] 270º |  |  | Time |  |  | VB | 60 | -120 |  | 60 | -120 | [9 empty] | 235.3172 | -37.0767 | -53.58 | 216.0417 | -68.1113 | -49.5615 | Rounding Fwd E/F | 3 | Ph-Ph: #REF!; B: 700; E: 90; B: #REF!; C: #REF!; D: #REF!; E: #REF! | [7 empty] | -37.0767 | -53.58 | #REF! | #REF!
|  |  |  | [ms] |  |  | VC | 60 | 120 |  | 60 | 120 | [9 empty] | 237 | -34.7953 | -53.58 | 218 | -63.4358 | -49.5615 | Rounding Rev Ph/Ph | 3 | Ph-Ph: #REF!; B: 875; E: 110; B: #REF!; C: #REF!; D: #REF!; E: #REF! | [7 empty] | -34.7953 | -53.58 | #REF! | #REF!
| Zone 3, | 5 | 5 | 430 | [17 empty] | 253.5 | -15.8711 | -53.58 | 244 | -24.1728 | -49.5615 | Rounding Rev E/F | 3 | Ph-Ph: #REF!; B: 1166.6667; E: #DIV/0!; B: #REF!; C: #REF!; D: #REF!; E: #REF! | [7 empty] | -15.8711 | -53.58 | #REF! | #REF!
| Not Testable | 7.121 | 5.6968 | 430 |  |  |  | Emergency Over-Current | [13 empty] | 270 | -9.8465e-15 | -53.58 | 270 | -9.108e-15 | -49.5615 | Ph-E Load Encroachment | OK | Ph-Ph: #REF!; B: 1750; E: #DIV/0!; B: #REF!; C: #REF!; D: #REF!; E: #REF! | [7 empty] | -9.8465e-15 | -53.58 | #REF! | #REF!
| Zone 5, | 6.7001 | 5.3601 | 1130 | [17 empty] | 278.8717 | 8.3633 | -53.58 | 309.9758 | -9.108e-15 | -49.5615 |  |  | B: 3500; E: #DIV/0!; B: #REF!; C: #REF!; D: #REF!; E: #REF! | [7 empty] | 8.3633 | -53.58 | #REF! | #REF!
| t5 | 0.2472 | 0.19776 | 1130 | [17 empty] | 292 | 13.6604 | -33.8108 | 290 | 18.0389 | -49.5615 | 4 | Voltage for Timing Tests | B: 4666.6667 | [7 empty] | 13.6604 | -33.8108 | #REF! | #REF!
| No Op | 0.23259 | 0.18607 | [18 empty] | PTT | 42.6131 | -10.6246 | PTT | 112.4864 | -28.046 | Spinner Value | 50 | Ph-Ph: 50; Ph-E: 50; Ph-Ph: 50 | [7 empty] | 42.6131 | -10.6246 | 112.4864 | -28.046
| Fault Voltage | 12.8592 | 9.5158 |  |  |  |  | Back-Up Over-Current | [13 empty] | 0 | 45.46 | 0 | 0 | 153.5315 | 0 | V Scaler | 1 | Ph-Ph: 1; Ph-E: 1; Ph-Ph: 1; A: Ang; B: Imp Ph-E | [7 empty] | 45.46 | 0 | 153.5315 | 0
[22 empty] | 10 | 47.7143 | 8.4133 | 4 | 156.4631 | 10.941 | Test V, X axis | 10.992 | Ph-Ph: 10.1676; Ph-E: 12.8592; Ph-Ph: 9.5158; A: 0 | [7 empty] | 47.7143 | 8.4133 | 156.4631 | 10.941
[22 empty] | 20 | 50.3726 | 18.3341 | 8 | 159.5394 | 22.4218 | Test Angle, +/- | 10.3815 | Ph-E: 12.0966; A: 90 | [7 empty] | 50.3726 | 18.3341 | 159.5394 | 22.4218
[22 empty] | 29.5028 | 53.5842 | 30.32 | 9.8789 | 161.0464 | 28.046 | Magnitude [V] | 30.4993 | Ph-E: 30.6813; A: 180 | [7 empty] | 53.5842 | 30.32 | 161.0464 | 28.046
[22 empty] | 40 | 36.134 | 30.32 | 12 | 131.9461 | 28.046 | Max Z, X axis. | 45.8 | Ph-Ph: 42.365; Ph-E: 53.58; Ph-Ph: 49.5615; A: 270 | [7 empty] | 36.134 | 30.32 | 131.9461 | 28.046
[22 empty] | 65 | 14.1384 | 30.32 | 51 | 22.7112 | 28.046 | Max Z, R axis. | 68.18 | Ph-Ph: 175.4563; Ph-E: 26.79; Ph-Ph: 54.8313 | [7 empty] | 14.1384 | 30.32 | 22.7112 | 28.046
[22 empty] | 90 | 1.8573e-15 | 30.32 | 90 | 1.718e-15 | 28.046 | Test Ve, R axis |  | Ph-Ph: 30.8803; Ph-Ph: 9.6503; A: 1.1*MaxReach; B: 210.7067 | [7 empty] | 1.8573e-15 | 30.32 | 1.718e-15 | 28.046
[22 empty] | 112 | -12.2501 | 30.32 | 110 | -10.2079 | 28.046 | [25 empty] | -12.2501 | 30.32 | -10.2079 | 28.046
[23 empty] | -12.2501 | 30.32 |  | -10.2079 | 28.046 | [25 empty] | -12.2501 | 30.32 | -10.2079 | 28.046
[5 empty] | Load Encroachment, Phase-Phase | [17 empty] | -12.2501 | 30.32 |  | -10.2079 | 28.046 | Z1 Test points | OK | D: Load Encroachment, Phase-Earth | [7 empty] | -12.2501 | 30.32 | -10.2079 | 28.046
[6 empty] | Load | Z1 | Z1B | Z2 | Z3 | Z4 | Z5 | [10 empty] | -12.2501 | 30.32 |  | -10.2079 | 28.046 | CrossCheck | OK | E: Load; F: Z1; A: Z1B; B: Z2; C: Z3; D: Z4; E: Z5 | [7 empty] | 71.6896 | -58.2184 | 146.0166 | -28.046
[5 empty] | 0 | 144 | 27.28 | 45.46 | 34.1 | 4.54 | 68.18 | 22.72 | [9 empty] | SOTF | 71.6896 | -58.2184 | SOTF | 146.0166 | -28.046 |  |  | D: 0; E: 99999; F: 76.7561; A: 153.5315; B: 120.625; C: 8.7815; D: 175.4563; E: 54.8313 | [7 empty] | 92.3514 | 0 | 153.5315 | 0
[5 empty] | 57 | 264.3953 | 85.2719 | 142.0989 | 106.5898 | 14.1911 | 213.1172 | 71.0182 | [9 empty] | 0 | 92.3514 | 0 | 0 | 153.5315 | 0 |  |  | Ph-E: Reverse; D: 57; E: 183606.0098; F: 239.9243; A: 479.909; B: 377.0498; C: 27.4492; D: 548.4416; E: 171.3918 | [7 empty] | 90.9484 | 16.0367 | 159.5394 | 22.4218
[5 empty] | 166 | -148.4084 | 26.3545 | 43.9177 | 32.9431 | 4.386 | 65.8669 | 21.9492 | [9 empty] | 10 | 90.9484 | 16.0367 | 8 | 159.5394 | 22.4218 |  |  | D: 166; E: -103060.3323; F: 74.152; A: 148.3226; B: 116.5326; C: 8.4836; D: 169.5036; E: 52.971 | [7 empty] | 80.3763 | 45.48 | 161.0464 | 28.046
[6 empty] | Char. Selection | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | 29.5028 | 80.3763 | 45.48 | 9.8789 | 161.0464 | 28.046 |  |  | E: Char. Selection; F: 0; A: 0; B: 0; C: 0; D: 0; E: 0 | [7 empty] | 39.0294 | 83.6988 | 131.9461 | 28.046
[22 empty] | 65 | 39.0294 | 83.6988 | 12 | 131.9461 | 28.046 | [25 empty] | 5.6572e-15 | 92.3514 | -146.0166 | 28.046
[22 empty] | 90 | 5.6572e-15 | 92.3514 | 90 | 1.718e-15 | 28.046
[22 empty] | 112 | -34.5955 | 85.6267 | 110 | -10.2079 | 28.046 | bar: Ph-E
[22 empty] | 140.9203 | -71.6896 | 58.2184 | 169.1274 | -146.0166 | 28.046 | bar: Ph-E
[22 empty] | 180 | -92.3514 | 1.1314e-14 | 180 | -153.5315 | 1.881e-14 |  |  | Ph-E: settings conflict with Load Encroachment!
[22 empty] | 209.5028 | -80.3763 | -45.48 | 189.8789 | -161.0464 | -28.046 |  |  | Ph-E: settings conflict with Load Encroachment!
[22 empty] | 270 | -1.6972e-14 | -92.3514 | 270 | -5.1541e-15 | -28.046 |  |  | A: Faulty Phase; B: 10.17; C: 9.5158
[22 empty] | 292 | 34.5955 | -85.6267 | 290 | 10.2079 | -28.046 |  |  | A: Healthy Phase; B: 60; C: 60; D: Earthed System; E: Non Earthed System; F: Non Earthed System
[22 empty] | 292 | 34.5955 | -85.6267 | 0 | 10.2079 | -28.046 | Ref Angle | 0 | Ph-E: R-E; A: TRUE; B: 10.17; C: 9.5158; D: 0; E: 0; F: 0
[23 empty] | 71.6896 | -58.2184 |  | 146.0166 | -28.046 |  |  | Ph-E: S-E; A: FALSE; B: 60; C: 60; D: -120; E: -146.8; F: -147
[22 empty] | 0 | 92.3514 | 0 |  |  |  | Load Plot |  | Ph-E: T-E; A: FALSE; B: 60; C: 60; D: 120; E: 146.8; F: 147
[22 empty] | 30 | 79.9787 | 46.1757 | 60 |  |  | 0 | 0
[22 empty] | 60 | 46.1757 | 79.9787 | 90 |  |  | 0 | 0 | Ph-E: Forward E/F Voltage; F: Reverse E/F Voltage
[22 empty] | 90 | 5.6572e-15 | 92.3514 | 120 |  |  | Voltage Plot |  | Ph-E: 10.17; A: 0; B: 10.17; C: 0; F: 9.5158; A: 0; B: 9.5158; C: 0
[22 empty] | 120 | -46.1757 | 79.9787 | 150 |  |  | 100 | 0 | B: -76.4325; C: -50; B: -77.0867; C: -50
[22 empty] | 150 | -79.9787 | 46.1757 | 180 |  |  | 0 | 0 | B: -76.4325; C: 50; B: -77.0867; C: 50
[22 empty] | 180 | -92.3514 | 1.1314e-14 | 210 |  |  | -50 | 86.6025 | B: 10.17; C: 0; B: 9.5158; C: 0
[22 empty] | 210 | -79.9787 | -46.1757 | 240 |  |  | -50 | -86.6025 | Ph-E: 91.3342; A: -146.8084; B: -76.4325; C: -50; F: 91.8823; A: -147.0317; B: -77.0867; C: -50
[22 empty] | 240 | -46.1757 | -79.9787 | 270 |  |  | 0 | 0 | B: 0; C: 0; B: 0; C: 0
[22 empty] | 270 | -1.6972e-14 | -92.3514 | 300 |  |  | Current Plot |  | Ph-E: 91.3342; A: 146.8084; B: -76.4325; C: 50; F: 91.8823; A: 147.0317; B: -77.0867; C: 50
[22 empty] | 300 | 46.1757 | -79.9787 | 330 |  |  | 24.7487 | -24.7487
[22 empty] | 330 | 79.9787 | -46.1757 | 360 |  |  | 0 | 0 |  |  | R-S | 100 | -150 | -86.6025 | -50 |  | R-S | 100 | -150 | -86.6025 | -50
[22 empty] | 360 | 92.3514 | -2.2629e-14 | Blinder 1 | 155.8848 | -62.9815 | 9.0587 | 33.8074 |  |  | S-T | 100 | 150 | -86.6025 | 50 |  | S-T | 100 | 150 | -86.6025 | 50
[22 empty] | Fwd Blinder 1 | 74.5939 | -30.1379 |  | -155.8848 | 62.9815 | -33.8074 | -9.0587
[23 empty] | -74.5939 | 30.1379 | Blinder 2 | 78.9309 | -148.4475 | 0 | 0
[22 empty] | Fwd Blinder 2 | -40.226 | 69.6735 |  | -78.9309 | 148.4475 | Current Lagging by 45 Deg.
[22 empty] | Rev Blinder 1 | 40.226 | -69.6735 | Scaler | 168.1272
[22 empty] | Scaler | 80.4521 | 0
[22 empty] | Load Encroachment | 0 | 0 | Load Encroachment | 0 | 0
[22 empty] | 60 | 0 | 0 | 60 | 0 | 0
[22 empty] | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | -60 | 0 | 0 | -60 | 0 | 0
[23 empty] | 0 | 0 |  | 0 | 0
|  | Phase-Phase | [5 empty] | Phase-Earth | [14 empty] | 0 | 0 |  | 0 | 0
|  | 1.7068 | 30 | 66.6667 | 66.6667 |  |  | 1.7068 | 30 | 66.6667 | 66.6667 | [11 empty] | 0 | 0 |  | 0 | 0
|  | 0.70321 | 30 | 66.6667 | 66.6667 |  |  | 0.70321 | 30 | 66.6667 | 66.6667 | [11 empty] | 0 | 0 |  | 0 | 0
[23 empty] | 0 | 0 |  | 0 | 0
[23 empty] | 0 | 0 |  | 0 | 0
|  | 0.66225 | 430 | 4.6512 | 4.6512 |  |  | 0.66225 | 430 | 4.6512 | 4.6512 | [10 empty] | Load Compensation | 4.167 | 16.1 | Load Compensation | 3.8545 | 14.8925
|  | 0.46553 | 430 | 4.6512 | 4.6512 |  |  | 0.46553 | 430 | 4.6512 | 4.6512 | [11 empty] | 31.5843 | 16.0638 |  | 80.7376 | 14.859
[23 empty] | Load Compensation |  |  | Load Compensation
|  | 0.43802 | 930 | 2.1505 | 2.1505 |  |  | 0.43802 | 930 | 2.1505 | 2.1505 | [11 empty] | Total Line | 16.6305 |  | Total Line | 15.3832
|  | 0.2472 | 930 | 2 | 2 |  |  | 0.2472 | 930 | 2.1505 | 2.1505 | [11 empty] | Top segment | 0 |  | Top segment | 0
|  | 0.23259 | [5 empty] | 0.23259 | [14 empty] | Bottom segment | 16.6305 |  | Bottom segment | 15.3832
|  | Min Op | 0.16 |  |  |  |  | Min Op | 0.16 | [13 empty] | R Co-ord | 31.5843 |  | R Co-ord | 80.7376
[23 empty] | X Co-ord | 16.0638 |  | X Co-ord | 14.859
|  |  | 430 | 4.6512 | 4.6512 |  |  |  | 430 | 4.6512 | 4.6512 | [10 empty] | Start | 75.4892 | 16.6305 | Start | 75.4892 | 15.3832
|  |  | 430 | 4.6512 | 4.6512 |  |  |  | 430 | 4.6512 | 4.6512 | [10 empty] | Mid Pt | 51.2236 | 20.6517 | Mid Pt | 42.9586 | 21.8535
|  | 6.7001 | 1130 | 1.7699 | 1.7699 |  |  | 5.3601 | 1130 | 1.7699 | 1.7699 | [10 empty] | Corner | 26.958 | 35.4346 | Corner | 10.4281 | 82.0935
|  | 0.2472 | 1130 | 1.7699 | 1.7699 |  |  | 0.19776 | 1130 | 1.7699 | 1.7699 | [10 empty] | Max Reach | 0 | 687.5 | Max Reach | 0 | 393.75
|  | 0.23259 | [5 empty] | 0.18607 | [13 empty] | Load Encroach | 0 |  | Load Encroach | 0
[22 empty] | Ze5 | 1 |  | Ze5 | 1
[22 empty] | Ze4 | 1 |  | Ze4 | 1
[22 empty] | Ze3 | 1 |  | Ze3 | 1
[22 empty] | 0 | 0 | 0 | 0 | 0 | 0
|  | -14 | 1.3011 | 5 | 5 | [16 empty] | 15 | 0 | 0 | 15 | 0 | 0
|  | -7.565 | 2.3909 | 5 | 5 | [16 empty] | 30 | 0 | 0 | 30 | 0 | 0
|  | 0 | 2.3701 | 5 | 5 | [16 empty] | 45 | 0 | 0 | 45 | 0 | 0
|  | 3 | 2.3733 | 5 | 5 | [16 empty] | 60 | 0 | 0 | 60 | 0 | 0
|  | 6 | 2.3831 | 5 | 5 | [16 empty] | 75 | 0 | 0 | 75 | 0 | 0
|  | 7.565 | 2.3909 | 5 | 5 | [16 empty] | 90 | 0 | 0 | 90 | 0 | 0
|  | 10 | 1.8126 | 5 | 5 | [16 empty] | 105 | 0 | 0 | 105 | 0 | 0
|  | 50 | 0.41089 | 5 | 5 | [16 empty] | 120 | 0 | 0 | 120 | 0 | 0
|  | 90 | 0.31476 | 5 | 5 | [16 empty] | 135 | 0 | 0 | 135 | 0 | 0
|  | 172.435 | [19 empty] | 150 | 0 | 0 | 150 | 0 | 0
|  | 110 | 0.33496 | 5 | 5 | [16 empty] | 165 | 0 | 0 | 165 | 0 | 0
[22 empty] | 180 | 0 | 0 | 180 | 0 | 0
[22 empty] | 195 | 0 | 0 | 195 | 0 | 0
[22 empty] | 210 | 0 | 0 | 210 | 0 | 0
[22 empty] | 225 | 0 | 0 | 225 | 0 | 0
| Emergency O/C | [6 empty] | Inverse Time E. Fault | [13 empty] | 240 | 0 | 0 | 240 | 0 | 0
|  | [A] | [ms] | Tol + | Tol - |  |  | [A] | [s] | Tol + | Tol - | [10 empty] | 255 | 0 | 0 | 255 | 0 | 0
| Phase | 3.6 | 130 | 19.2308 | 19.2308 | [16 empty] | 270 | 0 | 0 | 270 | 0 | 0
|  | 2.52 | 130 | 19.2308 | 19.2308 | [16 empty] | 285 | 0 | 0 | 285 | 0 | 0
|  | 2.28 | 930 | 2.6882 | 2.6882 | [16 empty] | 300 | 0 | 0 | 300 | 0 | 0
|  | 1.9275 | 930 | 2.6882 | 2.6882 | [16 empty] | 315 | 0 | 0 | 315 | 0 | 0
|  | 1.575 | 930 | 2.6882 | 2.6882 | [16 empty] | 330 | 0 | 0 | 330 | 0 | 0
|  | 1.425 | [19 empty] | 345 | 0 | 0 | 345 | 0 | 0
| Earth | [20 empty] | 360 | 0 | 0 | 360 | 0 | 0
|  | 0.475 | 930 | 2.6882 | 2.6882
|  | 0.325 | 930 | 2.6882 | 2.6882
|  | 0.175 | 930 | 2.6882 | 2.6882
0.15833
Back-Up O/C
|  | [A] | [ms] | Tol + | Tol -
Phase
Earth
|  | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| TurloughHill | Dunstown | 7SA612, 5A
| Measurands | MW:+322.3 | MVAr:+117.3
| In | 5 | 2025-05-15 15:55
| VfFwd | 10.992
| VfRev | 12.8592
| Vh | 60 | xls V: 27/10/2010
| Ve_F | 10.1676 | Fwd EF V
| Ve_R | 9.5158 | Rev EF V
| J_PU | 0.16 | Ph PU
| Je_PU | 0.16 | E PU
| FI1 | 1.707 | Z1
| FI2 | 0.703
| FI3 | Off | Z1B
| FI4 | Off
| FI5 | 0.662 | Z2
| FI6 | 0.466 | Forward
| FI7 | Off | Z3 or Z4
| FI8 | Off | TRUE
| FI9 | 0.438 | Z4 or NoOp
| FI10 | 0.247 | TRUE
| FI11 | 0.233
| Ft1 | 30
| Ft2 | 30
| Ft3 | Off
| Ft4 | Off
| Ft5 | 430
| Ft6 | 430
| Ft7 | Off
| Ft8 | Off
| Ft9 | 930
| Ft10 | 930
| RI1 | Off
| RI2 | Off
| RI3 | 6.7
| RI4 | 0.247
| RI5 | 0.233
| Rt1 | 430
| Rt2 | 430
| Rt3 | 1130
| Rt4 | 1130
| FIe1 | 1.707
| FIe2 | 0.703
| FIe3 | Off
| FIe4 | Off
| FIe5 | 0.662
| FIe6 | 0.466
| FIe7 | Off
| FIe8 | Off
| FIe9 | 0.438
| FIe10 | 0.247
| FIe11 | 0.233
| Fte_1 | 30
| Fte_2 | 30
| Fte_3 | Off
| Fte_4 | Off
| Fte_5 | 430
| Fte_6 | 430
| Fte_7 | Off
| Fte_8 | Off
| Fte_9 | 930
| Fte_10 | 930
| RIe1 | Off
| RIe2 | Off
| RIe3 | 5.36
| RIe4 | 0.198
| RIe5 | 0.186
| Rte_1 | 430
| Rte_2 | 430
| Rte_3 | 1130
| Rte_4 | 1130
| EM_I_1 | 3.6
| EM_I_2 | 2.52
| EM_I_3 | 2.28
| EM_I_4 | 1.9275
| EM_I_5 | 1.575
| EM_I_6 | 1.425
| EM_I_t1 | 130
| EM_I_t2 | 930
| EM_Ie_1 | No Test
| EM_Ie_2 | No Test
| EM_Ie_3 | 0.475
| EM_Ie_4 | 0.325
| EM_Ie_5 | 0.175
| EM_Ie_6 | 0.15833
| EM_Ie_t1 | No Test
| EM_Ie_t2 | 930
| Inv_Ang | 0
| InvEF_1 | No Test
| InvEF_2 | No Test
| InvEF_3 | No Test
| InvEF_4 | No Test
| InvEF_5 | No Test
| InvEF_6 | No Test
| InvEF_7 | No Test
| InvEF_8 | No Test
| InvEF_t1 | No Test
| InvEF_t2 | No Test
| InvEF_t3 | No Test
| InvEF_t4 | No Test
| InvEF_t5 | No Test
| InvEF_t6 | No Test
| InvEF_t7 | No Test
| PTTe_TX_V | 31.3863 | PTTe Tx
| PTTe_Tx_I_Limit | 1.2
| PTTe_TX_A1 | -14
| PTTe_TX_A2 | 0
| PTTe_TX_A3 | 4
| PTTe_TX_A4 | 8
| PTTe_TX_A5 | 9.8789
| PTTe_TX_A6 | 12
| PTTe_TX_A7 | 51
| PTTe_TX_A8 | 90
| PTTe_TX_A9 | 110
| PTTe_TX_Z1 | 115.93
| PTTe_TX_Z2 | 153.5315
| PTTe_TX_Z3 | 156.8452
| PTTe_TX_Z4 | 161.1073
| PTTe_TX_Z5 | 163.4702
| ZFS_Flt_V | 110 | Z4
| ZFS_I_Limit | 2.6
| PTT_TX_V | 110 | PTT Tx
| PTT_Tx_I_Limit | 4
| PTT_Dir | NOOP
| PTT_TX_A1 | -14
| PTT_TX_A2 | 0
| PTT_TX_A3 | 10
| PTT_TX_A4 | 20
| PTT_TX_A5 | 29.5028
| PTT_TX_A6 | 40
| PTT_TX_A7 | 65
| PTT_TX_A8 | 90
| PTT_TX_A9 | 112
| PTTe_TX_Z6 | 134.8938
| PTTe_TX_Z7 | 36.0885
| PTTe_TX_Z8 | 28.046
| PTTe_TX_Z9 | 29.8459
| ZFR_Flt_V | 110 | Rev Ph Start Z
| ZFR_I_Limit | 5.5
| PTT_TX_Z1 | 43.9177
| PTT_TX_Z2 | 45.46
| PTT_TX_Z3 | 48.4504
| PTT_TX_Z4 | 53.6054
| PTT_TX_Z5 | 61.5676
| PTT_TX_Z6 | 47.1695
| PTT_TX_Z7 | 33.4544
| PTT_TX_Z8 | 30.32
| PTT_TX_Z9 | 32.7012
| Dead_Time_1 | 1
| Dead_Time_3 | 0.6
| Meas_Ang | 180
| Meas_V | 57.7367
| Tol | 25
| WEI_UV | 35
| ZFSe_Flt_V | 36.7779 | Fwd E Start Z
| ZFSe_I_Limit | 1
| Start_V | 13.0906 | Carrier Start
| Start_I_Lim | 0.6914
| Start_Z1 | 68.18
| Start_Z2 | 45.8
| Start_Z3 | 22.72
| Start_Z4 | 53.58
| StartE_V | 33.6876
| StartE_I_Lim | 0.95421
| StartE_Z1 | 175.4563
| StartE_Z2 | 42.365
| StartE_Z3 | 54.8313
| StartE_Z4 | 49.5615
| DCEF_I | 0.1
| DCEF_V | 0.98266
| Alpha | 338
| Beta | 122
| ZFRe_Flt_V | 63 | Rev E Start Z
| ZFRe_I_Limit | 1.4
| SEF_V | 28.8684
| SEF_Vmin | 40
| SEF_Vmax | 75
| SEF_I | 0.008 | Amps
| SEF_t | 2.5 | s
| Z1e_Cycles | 5
| Z1Be_Cycles | 5
| Z2e_Cycles | 25
| Z3e_Cycles | 25
| Z4e_Cycles | 50
| Z5e_Cycles | 60
| Z1B_t | 30 | For AR on 7SA611
| CBF_I | 0.5
| CBF_t1 | 100
| CBF_t2 | 200
| CBF_t3 | 70
| Z1_Cycles | 5 | Z1 Plot
| Z1_V | 106.3039
| Z1_I_Lim | 7.3
| Z1B_Cycles | 5 | Z1B Plot
| Z1B_V | 110
| Z1B_I_Lim | 4
| Z2_Cycles | 25 | Z2 Plot
| Z2_V | 110
| Z2_I_Lim | 5
| Z3_Cycles | 25 | Z3 Plot
| Z3_V | 16.1122
| Z3_I_Lim | 9.5
| Z1e_V | 15.762
| Z1e_I_Lim | 1.2
| Z1Be_V | 31.3863
| Z1Be_I_Lim | 1.2
| Z2e_V | 24.6979
| Z2e_I_Lim | 1.2
| Z3e_V | 1.805
| Z3e_I_Lim | 1.2
| SOTF_V | 184.7028
| SOTF_I_Lim | 2.2
| SOTFe_V | 54.18
| SOTFe_I_Lim | 2.1
| PUTT_V | 110
| PUTT_I_Lim | 4
| PUTTe_V | 31.3863
| PUTTe_I_Lim | 1.2
| I_Ang | 90 | Timing Macros
| Max_On | 2
| ZPUTT_A1 | -14
| ZPUTT_A2 | 0
| ZPUTT_A3 | 10
| ZPUTT_A4 | 20
| ZPUTT_A5 | 29.5028
| ZPUTT_A6 | 40
| ZPUTT_A7 | 65
| ZPUTT_A8 | 90
| ZPUTT_A9 | 112
| ZPUTT_A10 | OFF
| ZPUTT_A11 | OFF
| ZPUTT_A12 | OFF
| ZPUTT_Z1 | 43.9177
| ZPUTT_Z2 | 45.46
| ZPUTT_Z3 | 48.4504
| ZPUTT_Z4 | 53.6054
| ZPUTT_Z5 | 61.5676
| ZPUTT_Z6 | 47.1695
| ZPUTT_Z7 | 33.4544
| ZPUTT_Z8 | 30.32
| ZPUTT_Z9 | 32.7012
| ZPUTT_Z10 | OFF
| ZPUTT_Z11 | OFF
| ZPUTT_Z12 | OFF
| ZPUTTe_A1 | -14
| ZPUTTe_A2 | 0
| ZPUTTe_A3 | 4
| ZPUTTe_A4 | 8
| ZPUTTe_A5 | 9.8789
| ZPUTTe_A6 | 12
| ZPUTTe_A7 | 51
| ZPUTTe_A8 | 90
| ZPUTTe_A9 | 110
| ZPUTTe_A10 | OFF
| ZPUTTe_A11 | OFF
| ZPUTTe_A12 | OFF
| ZPUTTe_Z1 | 115.93
| ZPUTTe_Z2 | 153.5315
| ZPUTTe_Z3 | 156.8452
| ZPUTTe_Z4 | 161.1073
| ZPUTTe_Z5 | 163.4702
| ZPUTTe_Z6 | 134.8938
| ZPUTTe_Z7 | 36.0885
| ZPUTTe_Z8 | 28.046
| ZPUTTe_Z9 | 29.8459
| ZPUTTe_Z10 | OFF
| ZPUTTe_Z11 | OFF
| ZPUTTe_Z12 | OFF
| ZSOTF_A1 | -39.0797
| ZSOTF_A2 | 0
| ZSOTF_A3 | 10
| ZSOTF_A4 | 29.5028
| ZSOTF_A5 | 65
| ZSOTF_A6 | 90
| ZSOTF_A7 | 112
| ZSOTF_A8 | 140.9203
| ZSOTF_A9 | 180
| ZSOTF_A10 | 209.5028
| ZSOTF_A11 | 270
| ZSOTF_A12 | 292
| ZSOTF_Z1 | 92.3514
| ZSOTF_Z2 | 92.3514
| ZSOTF_Z3 | 92.3514
| ZSOTF_Z4 | 92.3514
| ZSOTF_Z5 | 92.3514
| ZSOTF_Z6 | 92.3514
| ZSOTF_Z7 | 92.3514
| ZSOTF_Z8 | 92.3514
| ZSOTF_Z9 | 92.3514
| ZSOTF_Z10 | 92.3514
| ZSOTF_Z11 | 92.3514
| ZSOTF_Z12 | 92.3514
| ZSOTFe_A1 | -10.8726
| ZSOTFe_A2 | 0
| ZSOTFe_A3 | 8
| ZSOTFe_A4 | 9.8789
| ZSOTFe_A5 | 12
| ZSOTFe_A6 | 90
| ZSOTFe_A7 | 110
| ZSOTFe_A8 | 169.1274
| ZSOTFe_A9 | 180
| ZSOTFe_A10 | 189.8789
| ZSOTFe_A11 | 270
| ZSOTFe_A12 | 290
| ZSOTFe_Z1 | 148.6857
| ZSOTFe_Z2 | 153.5315
| ZSOTFe_Z3 | 161.1073
| ZSOTFe_Z4 | 163.4702
| ZSOTFe_Z5 | 134.8938
| ZSOTFe_Z6 | 28.046
| ZSOTFe_Z7 | 29.8459
| ZSOTFe_Z8 | 148.6857
| ZSOTFe_Z9 | 153.5315
| ZSOTFe_Z10 | 163.4702
| ZSOTFe_Z11 | 28.046
| ZSOTFe_Z12 | 29.8459
| Z4_Cycles | 50
| Z5_Cycles | 60
| Z1_A1 | -14
| Z1_A2 | OFF
| Z1_A3 | 0
| Z1_A4 | 8.5
| Z1_A5 | 17
| Z1_A6 | 26.958
| Z1_A7 | 37
| Z1_A8 | 63.5
| Z1_A9 | 90
| Z1_A10 | OFF
| Z1_A11 | 112
| Z1_Z1 | 26.3545
| Z1_Z2 | OFF
| Z1_Z3 | 27.28
| Z1_Z4 | 28.7336
| Z1_Z5 | 31.0719
| Z1_Z6 | 35.4346
| Z1_Z7 | 26.7524
| Z1_Z8 | 17.9901
| Z1_Z9 | 16.1
| Z1_Z10 | OFF
| Z1_Z11 | 17.3644
| Z3_A1 | 166
| Z3_A2 | OFF
| Z3_A3 | 180
| Z3_A4 | 189
| Z3_A5 | 198
| Z3_A6 | 200.2624
| Z3_A7 | 202
| Z3_A8 | 236
| Z3_A9 | 270
| Z3_A10 | OFF
| Z3_A11 | 292
| Z3_Z1 | 4.386
| Z3_Z2 | OFF
| Z3_Z3 | 4.54
| Z3_Z4 | 4.8003
| Z3_Z5 | 5.2289
| Z3_Z6 | 5.3707
| Z3_Z7 | 4.9652
| Z3_Z8 | 2.2436
| Z3_Z9 | 1.86
| Z3_Z10 | OFF
| Z3_Z11 | 2.0061
| Z1e_A1 | -14
| Z1e_A2 | -11.5666
| Z1e_A3 | 0
| Z1e_A4 | 4
| Z1e_A5 | 8
| Z1e_A6 | 10.4281
| Z1e_A7 | 12
| Z1e_A8 | 51
| Z1e_A9 | 90
| Z1e_A10 | OFF
| Z1e_A11 | 110
| Z1e_Z1 | 61.5591
| Z1e_Z2 | 74.274
| Z1e_Z3 | 76.7561
| Z1e_Z4 | 78.4127
| Z1e_Z5 | 80.5435
| Z1e_Z6 | 82.0935
| Z1e_Z7 | 71.629
| Z1e_Z8 | 19.1631
| Z1e_Z9 | 14.8925
| Z1e_Z10 | OFF
| Z1e_Z11 | 15.8483
| Z3e_A1 | 166
| Z3e_A2 | 168.3171
| Z3e_A3 | 180
| Z3e_A4 | 184.5
| Z3e_A5 | 189
| Z3e_A6 | 190.545
| Z3e_A7 | 193
| Z3e_A8 | 231.5
| Z3e_A9 | 270
| Z3e_A10 | OFF
| Z3e_A11 | 290
| Z3e_Z1 | 7.1118
| Z3e_Z2 | 8.4965
| Z3e_Z3 | 8.7815
| Z3e_Z4 | 8.9984
| Z3e_Z5 | 9.285
| Z3e_Z6 | 9.4013
| Z3e_Z7 | 7.6483
| Z3e_Z8 | 2.1984
| Z3e_Z9 | 1.7205
| Z3e_Z10 | OFF
| Z3e_Z11 | 1.8309
| RBB | 30 | 7SA611 Only
| Z1B_A1 | -14
| Z1B_A2 | OFF
| Z1B_A3 | 0
| Z1B_A4 | 10
| Z1B_A5 | 20
| Z1B_A6 | 29.5028
| Z1B_A7 | 40
| Z1B_A8 | 65
| Z1B_A9 | 90
| Z1B_A10 | OFF
| Z1B_A11 | 112
| Z1B_Z1 | 43.9177
| Z1B_Z2 | OFF
| Z1B_Z3 | 45.46
| Z1B_Z4 | 48.4504
| Z1B_Z5 | 53.6054
| Z1B_Z6 | 61.5676
| Z1B_Z7 | 47.1695
| Z1B_Z8 | 33.4544
| Z1B_Z9 | 30.32
| Z1B_Z10 | OFF
| Z1B_Z11 | 32.7012
| Z1Be_A1 | -14
| Z1Be_A2 | -10.8726
| Z1Be_A3 | 0
| Z1Be_A4 | 4
| Z1Be_A5 | 8
| Z1Be_A6 | 9.8789
| Z1Be_A7 | 12
| Z1Be_A8 | 51
| Z1Be_A9 | 90
| Z1Be_A10 | OFF
| Z1Be_A11 | 110
| Z1Be_Z1 | 115.93
| Z1Be_Z2 | 148.6857
| Z1Be_Z3 | 153.5315
| Z1Be_Z4 | 156.8452
| Z1Be_Z5 | 161.1073
| Z1Be_Z6 | 163.4702
| Z1Be_Z7 | 134.8938
| Z1Be_Z8 | 36.0885
| Z1Be_Z9 | 28.046
| Z1Be_Z10 | OFF
| Z1Be_Z11 | 29.8459
| Vh_e | 60
| Vh_e_Ang | 120
| Rev_Vh_e | 60
| Rev_Vh_e_Ang | 120
| Test_Ve_Fwd_R | 30.8803
| FIe1_R | 0.41 | R-Axis Timing
| FIe2_R | 0.26 | (7SA611 only)
| FIe3_R | 3.62
| FIe4_R | 0.18
| Z5_A1 | 166
| Z5_A2 | OFF
| Z5_A3 | 180
| Z5_A4 | 206.5
| Z5_A5 | 233
| Z5_A6 | 235.3172
| Z5_A7 | 237
| Z5_A8 | 253.5
| Z5_A9 | 270
| Z5_A10 | 278.8717
| Z5_A11 | 292
| Z5_Z1 | 21.9492
| Z5_Z2 | OFF
| Z5_Z3 | 22.72
| Z5_Z4 | 29.3019
| Z5_Z5 | 58.5837
| Z5_Z6 | 65.1575
| Z5_Z7 | 63.8868
| Z5_Z8 | 55.8812
| Z5_Z9 | 53.58
| Z5_Z10 | 54.2288
| Z5_Z11 | 36.4661
| Z5e_A1 | 166
| Z5e_A2 | OFF
| Z5e_A3 | 180
| Z5e_A4 | 197
| Z5e_A5 | 214
| Z5e_A6 | 216.0417
| Z5e_A7 | 218
| Z5e_A8 | 244
| Z5e_A9 | 270
| Z5e_A10 | OFF
| Z5e_A11 | 290
| Z5e_Z1 | 52.971
| Z5e_Z2 | OFF
| Z5e_Z3 | 54.8313
| Z5e_Z4 | 62.4528
| Z5e_Z5 | 80.729
| Z5e_Z6 | 84.2347
| Z5e_Z7 | 80.5012
| Z5e_Z8 | 55.1422
| Z5e_Z9 | 49.5615
| Z5e_Z10 | OFF
| Z5e_Z11 | 52.7422
| Open_Line | 90 | For SOTF
| Gen_Trafo | 0 | For SOTF
| DIFI1 | 1.02
| Diff_HS | 6.8
| Diff_t | 30
| TDIFG | 80 | PU delay for 1-Phase faults
| DIFC | 0 | dummy value for test plan compatability
| NomV | 100 | dummy value for test plan compatability
| DIFGI | 0 | dummy value for test plan compatability
| RBB_t | 0 | dummy value for test plan compatability
Note on C61: White Text on Grey Background indicates NO OP because test current is less than setting for Min. Iph>.
Note on D61: White Text on Grey Background indicates NO OP because test current is less than setting for Min. Iph>.
Note on C63: If test currents are too high to time all zones in one macro, reduce the test voltage to test inner Zones.

## 7SD522 (hidden)
Outlet: | Dunstown |  |  |  | Example | [19 empty] | Op Time | 25 | VT connected | FALSE | Comms: | TRUE
[25 empty] | Differential Prot. |  |  | Warning | Long Time
| CT Primary | 1800 |  |  | VT Primary [kV] | 220 | [22 empty] | Standard
| CT Sec. | 5 |  |  | VT Sec. [V] | 100 | [20 empty] | Star to Bus | TRUE | Very
[27 empty] | CT Correction | 0 | Extremely
Differential |  | @ Dunstown |  |  |  | At Dunstown | [18 empty] | 2Terminal | TRUE |  |  | Extremely | 80 | 2
F> PU [A] | 1 | 0.36 | 0.072 |  |  | CT Pri. | 1000 | CT Pri. | 1000 | [15 empty] | Varying |  |  |  | Long | 120 | 1
FF>> PU[A] | 6.8 | 12.24 | 2.448 |  |  | CT Sec. | 5 | CT Sec. | 1 |  |  |  |  | Inverse (Non-Standard] | [10 empty] | Fixed |  |  |  | Standard | 0.14 | 0.02
Full Scale I | 500 | 500 | 500 | [21 empty] | Varying | 180 |  |  | Very | 13.5 | 1
[0251] k_alf/k_alf nominal | 1.5 | 1.5 | [22 empty] | Test Point | 3 |  |  | Selection | k | a
[0253] CT Error at k_alf/k_alf nominal | 2% | 2% | [26 empty] | Standard | 0.14 | 0.02
[0254] CT Error at k_alf nominal | 10% | 10% | [11 empty] | OCI [A] | 4 | EFI [A] | 0.5 | [7 empty] | Plausability |  |  |  | Very | 13.5 | 1
VT Ratio | 2200 | [12 empty] | TOCI | 2 | TEFI [s] | 0.2 | [7 empty] | E/F is switched Off. No test points have been defined in the Test Plan.
0% |  | 0% | 0% | [25 empty] | OC Inverse |  | EF Inverse
[25 empty] | CT | CT factors |  |  | [A] | [s] | [A] | [s]
GPS Tests: | [25 empty] | 1.8 |  |  | 4.6 | 100.0304 | 0.575 | 18
[25 empty] | VT | 0.36 |  |  | 8 | 20.0581 | 1 | 2.7
|  | Test Point: | 3 | [21 empty] | 110 |  |  |  | 20 | 8.5594 | 2.5 | 0.675
|  | Balance |  | No Load |  |  |  | No Load |  |  |  | No Load |  | Target |  | No Load |  |  |  | No Load |  |  |  |  | 100 |  |  |  | 30 | 6.8092 | 5 | 0.3
|  | 7.875 | -180 | 0 | -180 | 7.875 | 163.0824 | 0 | -180 | 7.875 | 162.1316 | 0 | -180 | 7.875 | 161.1807 | 0 | -180 | 7.875 | 160.2298 | 0 | -180 | 7.875 | 159.279
|  | 7.875 | -360 | 0 | -360 | 7.875 | -16.9176 | 0 | -360 | 7.875 | -17.8684 | 0 | -360 | 7.875 | -18.8193 | 0 | -360 | 7.875 | -19.7702 | 0 | -360 | 7.875 | -20.721
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | Local | Remote | Angle |  | Ang Offset | Test I | Rest/Diff | 110% | Ang Limit | Current | Round
[26 empty] | 0 | 1.02 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0.2204 | 0.24244 | #DIV/0! | 0 | 3
|  | Balance |  | No Load |  |  |  | No Load |  |  |  | No Load |  |  |  | No Load |  |  |  | No Load | [5 empty] | 1 | 1.35 | 1.35 | 169.2039 | 169.2039 | 0.81268 | 6.75 | 0.254 | 0.2921 | 167.5786 | 6.75 | 3
|  | 7.875 | -180 | 0 | -180 | 7.875 | 163.0824 | 0 | 163.0824 | 7.875 | 162.1316 | 0 | 163.0824 | 7.875 | 161.1807 | 0 | 163.0824 | 7.875 | 160.2298 | 0 | 163.0824 | 7.875 | 159.279 |  |  | 2 | 1.575 | 1.35 | 167.7252 | 167.7252 | 0.91655 | 6.75 | 0.3845 | 0.42295 | 165.8921 | 6.75 | 3
|  | 0 | -180 | 0 | -180 | 0 | 163.0824 | 0 | 163.0824 | 0 | 162.1316 | 0 | 163.0824 | 0 | 161.1807 | 0 | 163.0824 | 0 | 160.2298 | 0 | 163.0824 | 0 | 159.279 |  |  | 3 | 1.575 | 1.575 | 161.1807 | 161.1807 | 0.95087 | 7.875 | 0.515 | 0.5665 | 159.279 | 7.875 | 3
|  | 0 | -180 | 0 | -180 | 0 | 163.0824 | 0 | 163.0824 | 0 | 162.1316 | 0 | 163.0824 | 0 | 161.1807 | 0 | 163.0824 | 0 | 160.2298 | 0 | 163.0824 | 0 | 159.279 |  |  | 4 | 3.15 | 3.15 | 164.859 | 164.859 | 0.76218 | 15.75 | 0.83 | 0.913 | 163.3346 | 15.75 | 2
[26 empty] | 5 | 6.3 | 6.3 | 166.692 | 166.692 | 0.66888 | 31.5 | 1.46 | 1.606 | 165.3543 | 31.5 | 2
[26 empty] | 6 | 9.45 | 9.45 | 167.3023 | 167.3023 | 0.63791 | 47.25 | 2.09 | 2.299 | 166.0265 | 47.25 | 2
After Energisation (fed from one end only): | [25 empty] | 7 | 12.285 | 12.285 | 167.5838 | 167.5838 | 0.62363 | 61.43 | 2.657 | 2.9227 | 166.3365 | 61.425 | 2
|  | Voltage [kV] | 120 |  |  |  | 0.2 | 0.2 | 0.2204 | 0.2204
|  | Charging Current [kA] | 0.04 |  |  |  | 9.52 | 9.52 | 0.254 | 0.254 | [8 empty] | Increments [mA]: | 10 |  |  | Rest | 0.2
|  | Optimum DIFC (100%) | 0.2037 |  |  |  | 0.2 | 6.8 | 0.3845 | 0.3845 | [8 empty] | Local | 0 | 0 |  | Diff | 0 |  |  | Spinners | Times Nom. | Angles
|  | Error [A] | 204.6667 |  |  |  | 9.52 | 6.8 | 0.515 | 0.515 | [8 empty] | Remote | 0 | 175.6 |  | Stable |  |  | Local End | 0 | 0 | 0 |  | 0 | 0
[7 empty] | 0.2 | 0 | 0.83 | 0.83 | [15 empty] | Remote End | 0 | 0 | #DIV/0! |  | 0 | 0
[9 empty] | 1.46 | 1.46 | [15 empty] | Angle | 878 |  | #DIV/0! | Diff | 0 | 0
[9 empty] | 2.09 | 2.09 | [19 empty] | Polar | 0 | #DIV/0!
[9 empty] | 2.657 | 2.657
[16 empty] | Inverse |  |  |  |  | Inverse E/Fault, A/Ph
[16 empty] | [A] | [s] | [A] | [s] |  | [A] | [s] | Tol = 0.1s
[16 empty] | 4.6 | 100.0304 | 0.575 | 18 |  | 1.6667 | 0.3 | 33.3333 | 33.3333
[16 empty] | 8 | 20.0581 | 1 | 2.7 |  | 0.83333 | 0.675 | 14.8148 | 14.8148
[16 empty] | 20 | 8.5594 | 2.5 | 0.675 |  | 0.33333 | 2.7 | 3.7037 | 3.7037
[16 empty] | 30 | 6.8092 | 5 | 0.3 |  | 0.19167 | 18 | 0.55556 | 0.55556
Charging Compensation
Balance |  | No Load |  | #REF! |  | No Load |  | #REF! |  | No Load |  | #REF! |  | No Load |  | #REF! |  | No Load |  | #REF!
0 | 0 | 0 | 0 | #REF! | 0 | 0 | 0 | #REF! | 0 | 0 | 0 | #REF! | 0 | 0 | 0 | #REF! | 0 | 0 | 0 | #REF! | 0
0 | -120 | 0 | -120 | #REF! | -120 | 0 | -120 | #REF! | -120 | 0 | -120 | #REF! | -120 | 0 | -120 | #REF! | -120 | 0 | -120 | #REF! | -120
0 | -240 | 0 | -240 | #REF! | -240 | 0 | -240 | #REF! | -240 | 0 | -240 | #REF! | -240 | 0 | -240 | #REF! | -240 | 0 | -240 | #REF! | -240
57.737 | 0 | 57.737 | 0 | 57.737 | 0 | 57.737 | 0 | 57.737 | 0 | 57.737 | 0 | 57.737 | 0 | 57.737 | 0 | 57.737 | 0 | 57.737 | 0 | 57.737 | 0
57.737 | -120 | 57.737 | -120 | 57.737 | -120 | 57.737 | -120 | 57.737 | -120 | 57.737 | -120 | 57.737 | -120 | 57.737 | -120 | 57.737 | -120 | 57.737 | -120 | 57.737 | -120
57.737 | 120 | 57.737 | 120 | 57.737 | 120 | 57.737 | 120 | 57.737 | 120 | 57.737 | 120 | 57.737 | 120 | 57.737 | 120 | 57.737 | 120 | 57.737 | 120 | 57.737 | 120
Metering
[8 empty] | Load | 1.3889
|  | Tol | 30 |  |  |  |  | Angle | -15
[8 empty] | 1.3889 | 345
|  | CT_Ratios | 1800/5 | 1000/5 |  |  |  | 1.3889 | 225
|  | NomV | 57.74 | Phase Voltage |  |  |  | 1.3889 | 105
[8 empty] | 57.74 | 0
|  | DIFI2 | 6.8 |  |  |  |  | 57.74 | -120
|  | DIFC | 0.09 |  |  |  |  | 57.74 | 120
[8 empty] | MW | -184.03
[8 empty] | MVAr | -49.31
|  | RBB_t | 8 | Add on For RBB |  |  |  | Va [kV] | 220
[8 empty] | Ia [kA] | 500
[8 empty] | Ia1 [kA] | 0.5
[8 empty] | Id [kA] | 0
[8 empty] | pf | 0.96593
[8 empty] | Rest | 0.204
Note on C20: Orange background indicates clipping of transferred current
Note on AJ24: Additional 5% restraining added due to additional standing restraint.
Comms:
Terminals:

## EF calcs
Open Delta |  |  |  | Max/Min V Ratio | 0.99996 |  |  |  | kV
0.0029335 | 0 |  |  |  |  | 180 Deg Shift |  | Primary | 38.5
33.3353 | 0 |  | R | 57.7367 | 0 | 57.7367 | 180 |  | 22.2286
33.3338 | -119.9985 |  | S | 57.7342 | -119.9985 | 57.7342 | 60.0015 |  | 22.2277
33.3338 | 119.9985 |  | T | 57.7342 | 119.9985 | 57.7342 | 299.9985 |  | 22.2277
[8 empty] | NDV | 0
Forward Timing |  |  |  | 0 | 0 | 0 | 0
R Phase | 57.7367 | 0 |  | 57.7367 | 0 | 33.3353 | 0
% Earth Fault |  |  |  | -28.8658 | -50 | 16.6691 | -28.8684
0 |  |  |  | -28.8658 | 50 | 0.0029335 | 0
|  |  |  | 57.7367 | 0
S Phase | 57.7342 | -119.9985 |  | -28.8658 | -50
|  |  |  | 0 | 0
T Phase | 57.7342 | 119.9985 |  | -28.8658 | 50 | -16.6662 | -28.8684
[6 empty] | -16.6662 | 28.8684
R-S | 100 | -150 |  | -86.6025 | -50
S-T | 100 | 150 |  | -86.6025 | 50
Open Delta
|  |  |  | 0.0029335 | 0
Reverse Timing |  |  |  | 0 | 0
R Phase | 4.7771 | 0 |  | 4.7771 | 0
% Earth Fault |  |  |  | -81.8254 | -50
91.726 |  |  |  | -81.8254 | 50
|  |  |  | 4.7771 | 0
S Phase | 95.8926 | -148.5727 |  | -81.8254 | -50
|  |  |  | 0 | 0
T Phase | 95.8926 | 148.5727 |  | -81.8254 | 50
R-S | 100 | -150 |  | -86.6025 | -50
S-T | 100 | 150 |  | -86.6025 | 50
Note on B13: Simcox_O: Do not move from B13, This cell is forced to test voltage by 'ProTesT' button
Note on B31: Simcox_O: Do not move from B31, This cell is forced to test voltage by 'ProTesT' button