## Settings
Station: | TH |  | Feeder: | Duns |  |  |  | Max Load [MVA]: | 107 | [7 empty] | 2011-08-25 | CT Connections | TRUE |  | Linked Parameters |  |  |  | Max Load current | 0.4493 | SOTF |  |  |  | AR Mode
[13 empty] | CT Connections: | [7 empty] | 8 | 120 | 22.7 | 120 |  |  | OC | On(1) | 3 |  | Disable(1)
VT Pri. [kV] | 110 | [17 empty] | 1A | GRZ100 | Direction Limits | [5 empty] | Z2 | Off(0) | Off |  | SPAR(2)
VT Sec. V | 100 | [11 empty] | Ir, Is, It, In | 2, 4, 6, 7 | [5 empty] | GRZ100xxx | Phase - Phase |  | Phase - Earth |  | Delta Ang |  | Z3 | Off(0) |  |  | TPAR(3)
CT Pri. A | 1250 | [11 empty] | Starpoint | 1, 3, 5, 8 |  | Delta Angle: | 3 | In= | 1 | 1 | -30 | 120 | -30 | 120 | 5 |  | ZR1 | Off(0) | Off |  | SPAR&TPAR(4)
[18 empty] | Type= | GRZ100 | [7 empty] | ZR2 | Off(0) |  |  | Selection | 3
[18 empty] | Op.Time [ms] | 28 |  |  | Healthy V, Ph Flts | 57.7367 |  |  |  |  | Fev OC Only 'On' | TRUE |  | TPAR(3) | OK
[22 empty] | Healthy V, E Flts | 63.51 | 120 | 63.5104 | 120 |  | Fwd OC Only 'On' | TRUE |  | TRR Min | 0.7
Protection Scheme |  |  |  |  | Z1S | 7.58 |  | ZBS-angle | 30 | TZ3S, TZ3G | 4.5 | Z3G | 37.6 | OCH(A) | 3 | UVCV | 52% | Starpoint= | 0 | Busbar | RBB | FALSE | [5 empty] | Ph-Ph | Ph-E |  | AR Effective | OK
BLZONE |  | OCBT |  |  | Z1S q 1 | 0 |  | BFRS | 25 | TZR1S, TZR1G | 0.5 | ZBG q | 30 | TSOTF | 5 | ZNDG | 51.5 | Gen. Trafo | FALSE |  |  |  |  | PTT Zone Sel | Z2(1) |  | PSB_Fwd_X | 29.5 | 47.6 |  | AR Setting Discrepancy | OK
Z1CNT |  | EFBT |  |  | Z1S q 2 | 90 |  | BFLS-angle | 120 | TZR2S, TZR2G | 1.1 | BFRG | 100 |  |  | UVCZ | 7.8 | Min. Iph> | 0.12 | [5 empty] | Z3(2) |  | PSB_Fwd_R | 35 | 110
PSB-Z1 'Off', All other zones 'On' |  | DEFFEN |  |  | Z1XS | 9.34 |  | ZR1S | 5.4 | TZNDS, TZNDG | 10 | BFLG | 120 | DEFFI | 0.1 | UVC q | 66 | Ang.of Inc | 75 |  |  |  |  | Selection | Z2(1) |  | PSB_Rev_X | 36.79 | 58.22 |  | DEFFEN | Off(0)
SOTF OC |  | DEFREN |  |  | BFR1S | 13.6 |  | ZR2S | 26.79 | Z1G | 7.58 | ZR1G | 6.7 | DEFFV | 1.7 | UVFS | 88 | Resistive Blinder | COM(1) | Teleprotection | 2 Z1-EXT (O/R without Teleprot.) | [5 empty] | PSB_Rev_R | 18 | 32.7 |  | DEFREN | Off(0)
SOTF Z2 |  | BCDEN |  |  | BFRXS | 10.5 |  | Z4S | 23.4 | Z1XG | 9.34 | ZR2G | 48.22 | DEFRI | 0.1 | UVLS | 70 |  | IND(2) |  | 3 PUP (Permissive Underreach) |  |  |  |  | Z1CNT | Fault Model Scalers | 28 | 71 |  | Display DCEF | FALSE
SOTF Z3 |  | ZONSEL |  |  | Z2S | 10.57 |  | BRRS | 8 | Z1G q 1 |  | Z4G | 41.4 | DEFRV | 1.7 | UVFG | 29 | Selection | IND(2) |  | 4 POP (Permissive Overrreach) |  |  |  |  | 1(1) | Max reach | 16.0369 | 51.4133 |  | 1
SOTF R1 |  |  |  |  | BFR2S | 17 |  | ZNDS | 44.2 | Z1G q 2 |  | BRRG | 22.7 | DEF_Angle | 48 | UVLG | 40 | Zone Restive Reach |  |  | 7 POP+DEF (POTT + DCEF) |  |  |  |  | 2(2) |  |  |  |  | Em. OC | On(1)
SOTF R2 |  | ECHO |  |  | Z3S | 19.5 |  | BNDS | 18 | BFR1G | 65.1 | Krs (%) | 291% |  |  |  |  | Z1 | 13.6 |  | 10 PUP+DEF (PUTT + DCEF) |  |  |  |  | 1(1) |  |  |  |  | Em. EF | On(1)
ZR1BT |  | WKIT | [5 empty] | TZ1S, TZ1G | 0 | BFRXG | 32.7 | [6 empty] | Z1X | 10.5 |  | Selection | 4 POP (Permissive Overrreach) |  |  | Z1 Time | 0 |  |  |  |  | Echo | On(1)
ZR2BT | [7 empty] | TZ2S, TZ2G | 0.4 | Z2G | 10.57 |  |  | OC | 3 | TDEFF | 0 | Z2 | 17 |  | 4 | 3 POTT |  |  | Z1 Time bypassed | OK |  |  |  |  | WKIT | Off(0)
ZNDBT | [7 empty] | ZNDG | 51.5 | BFR2G | 100 | Kxs (%) | 378% | TOC | 1 | TDEFR | 0 | Z3 | 25 |  |  |  | Test | Test
[8 empty] | BNDG | 45.5 |  |  |  |  | EF | 2 | TREBK | 0.1 |  | Effective Min I> for EF | 0.24 | Zone 1 | Zone 1X | Zone 2 | Zone 3 | Zone R1 | Zone R2 | Zone 4 (Echo) | Zone ND | SOTF | Load | PSB
[14 empty] | TEF | 1 |  |  | Off(0) |  | Zone Active (Check Box) |  | FALSE | TRUE | TRUE | On(1) | On(1) |  | Off(0)
[12 empty] | PSBSZ | 10 | EFL | 0.2 |  |  | On(1) |  | Display Ph-Ph |  | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | TRUE
AutoReclose Mode | [11 empty] | PSBGZ | 10 | EFL Multiplier | 1.2 |  |  |  |  | Display Ph-E |  | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE |  | TRUE | FALSE | FALSE
TEVLV | 0.9 | [18 empty] | Plot Ph-Ph Zones |  | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
TTPR1 | 0.7 | [18 empty] | Plot Ph-E Zones |  | 0 | 1 | 1 | 1 | 1 | 0 |  | 1 | 0
TSPR1 | 1 | [18 empty] | Convert for CT Starpoint
TRR | 1 | [18 empty] | CTStarPoint | Dir.1 | Dir.1B | Dir.2 | Dir.3 | Dir.4 | Dir.5 | Dir.6 |  | Display | Zph | Ze
TSUC | 0.5 | [18 empty] | 0 | 0 | 0 | 0 | 0 | 180 | 180 | 180 |  | Max Reach | FALSE | FALSE
[20 empty] | Scheme: | Normal | Scheme | 0
1
[18 empty] | Inverse Time E/F |  | FALSE | [5 empty] | Compensated E/F
[18 empty] | Extremely Inverse | 80 | 2 | [5 empty] | R | X
[18 empty] | Long Time Inverse | 120 | 1 |  |  |  |  | Z1 | 65.1 | 14.6041
[18 empty] | Normal Inverse | 0.14 | 0.02 |  |  |  |  | Z1X | 32.7 | 17.9951
[18 empty] | Very Inverse | 13.5 | 1 |  |  |  |  | Z2 | 100 | 20.3649
[18 empty] | Normal Inverse | 0.14 | 0.02 |  |  |  |  | Z3 | 100 | 37.6
[18 empty] | I/Ie | A/Ph | Time |  |  |  |  | ZR1 | 22.7 | 12.9087
[18 empty] | 20 | 0.066667 | 0.48147 |  |  |  |  | ZR2 | 22.7 | 48.22
[18 empty] | 10 | 0.033333 | 0.62212 |  |  |  |  | Z4 | 22.7 | 41.4
[18 empty] | 8 | 0.026667 | 0.68735
[18 empty] | 6 | 0.02 | 0.79544 |  | Generic | Zone 1 | Zone 1B | Zone 2 | Zone 3 | Zone 4 | Zone 5 | Zone 6
[18 empty] | 4 | 0.013333 | 1.024 |  | Specific | Zone 1 | Zone 1X | Zone 2 | Zone 3 | Zone R1 | Zone R2 | Zone 4
[18 empty] | 2 | 0.0066667 | 2.0338 |  | R |  |  | 17 | 25 | 8 | 8 | 8
[18 empty] | 1.5 | 0.005 | 3.4668 |  | X |  |  | 10.57 | 19.5 | 5.4 |  | 23.4
[18 empty] | 1 | 0.0033333 |  |  | RE | 65.1 | 32.7 | 100 | 100 | 22.7 | 22.7 | 22.7
[22 empty] | t | 0 | TZ2S, TZ2G | 0.4 | 4.5 | 0.5
Back-Up OverCurrent
[18 empty] | Ph Setting | FALSE | FALSE
[18 empty] | EF Setting | FALSE | FALSE
1-Ph Fault Model
[22 empty] | 57.7367 | 0 | 23.9607 | 0
[22 empty] | 57.7367 | -120 | 57.7367 | -120 | TRUE | 83
[22 empty] | 57.7367 | 120 | 57.7367 | 120 | OK | OK
[22 empty] | 0 | 0 | 0.466 | 148
[22 empty] | 0 | 0 | 0 | 0
[22 empty] | 0 | 0 | 0 | 0
[18 empty] | Load Angle | 45
[18 empty] | Basic Dir. | 1 |  |  | 2-Ph Fault Model |  |  | 42.5507 | 3-Ph Fault Model
[18 empty] | Max Rch |  |  |  | 57.7367 | 150 | 39.1871 | 132.5507 | 57.7367 | 0 | 30.6005 | 0
[22 empty] | 57.7367 | 30 | 39.1871 | 47.4493 | 57.7367 | -120 | 30.6005 | -120
[12 empty] | 43.6009 | 27.2449 |  |  |  |  | 1 |  |  |  | 57.7367 | 270 | 57.7367 | 270 | 57.7367 | 120 | 30.6005 | 120
[12 empty] | #N/A | #N/A |  |  |  |  | 0 |  |  |  | 0 | 0 | 3.305 | 282 | 0 | 0 | 3.8164 | 102
[18 empty] | 1 |  |  |  | 0 | 0 | 3.305 | 102 | 0 | 0 | 3.8164 | 342
[22 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 3.8164 | 222
|  |  | 3.3342 | 15.6864 | [13 empty] | Resultant | 1 |  |  | Evolving I | OK | OK | OK | TRUE | 106 | OK | OK
|  |  | #N/A | #N/A
[19 empty] | 3Uo | #N/A |  |  | R-S |  | S-T |  | T-R
|  |  | #N/A | #N/A | [7 empty] | DCEF: Forward PU |  | #N/A | #N/A |  |  |  | Vr | 56.87 | 0 | #N/A | #N/A |  | #N/A |  | #N/A
Fault Model | [7 empty] | Fault Locator |  |  |  | Fault Model | [6 empty] | Vs | -28.87 | -50.0043 | #N/A | #N/A |  | #N/A |  | #N/A
Impedance | 16.0369 | [5 empty] | Vr | 56.87 | 0 |  |  | Impedance | 51.4133 |  |  |  |  | Starpoint Correction | Vt | -28.87 | 50.0043 | #N/A | #N/A |  | #N/A |  | #N/A
Angle | 78 |  | Load |  |  |  | Vs | 57.74 | -120 |  |  | Angle | 32 |  |  |  |  | 319 | Ir | 0.22641 | -0.19682 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Fault Voltage | 53 |  | MW | 10 |  |  | Vt | 57.74 | 120 |  |  | Fault Voltage | 23.9607 |  |  |  |  | 129 | Is | 0 | 0 | #N/A | R-S | FALSE | S-T | FALSE | T-R | TRUE
Fault Current | 3.305 |  | Mvar | 10 |  |  | Ir | 0.3 | 139 |  |  | Fault Current | 0.466 |  |  |  |  | 180 | It | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[7 empty] | Is | 0 | -51 |  |  | E/F loops | released | [5 empty] | 3Io | #N/A |  |  | Ph-Ph Selection | FALSE
[7 empty] | It | 0 | 0
[7 empty] | 3Uo | 0 | 0 | [13 empty] | R-E |  | S-E |  | T-E
[7 empty] | 3Io | #N/A | #N/A | [13 empty] | #N/A |  | #N/A |  | #N/A
[8 empty] | E/F loops | #N/A | [13 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[23 empty] | R-E | TRUE | S-E | FALSE | T-E | FALSE
[23 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[23 empty] | E/F Selection | FALSE
CB Fail Settings:
[19 empty] | [3902] I > | 0.1 | [3905] T1, Retrip | 0.12 | [3906] T2, Busbar | 0.24 |  | [3907] T3, CB Def. | 0.04
Not defined:
| Descriptions | [16 empty] | TZ1XS, TZ1XG | 0
| AR Timers |  | CBF
| TMPR1 |  | OCBF | [17 empty] | [3303] Ie> | 0.01
| TW1 |  | TBF1 | [17 empty] | [3304] Delay Time | 2
| TRDY1 | 10 | TBF2
Zone Summary:
| Forward |  |  |  | Reverse |  |  | Non-Dir.
Reaches/Times | Zone 1 | Zone 1 Ext. | Zone 2 | Zone 3 | Zone R1 | Zone R2 |  |  | Zone 4 | Zone FS
(Ohms/Phase) | Forward | Off | Forward | Forward | Reverse | Reverse |  | Off
Ph Resistive | 13.6 | 10.5 | 17 | 25 | 8 | 8 |  | 18
Ph Reactive | 7.58 | 9.34 | 10.57 | 20 | 5.4 | 26.79 |  | 44.2
E/F Resistive | 65.1 | 32.7 | 0 | 4 | 22.7 | 22.7
E/F Reactive
Time [s] | 0 | 0 | 0.4 | 0.9 | 0.5 | 1.1 |  | 10
Evolving Fault
1-Phase | 57.7367 | 0 | 23.9607 | 0 | 39.1871 | 342.5507 | 30.6005 | 0
| 57.7367 | -120 | 57.7367 | -120 | 39.1871 | 257.4493 | 30.6005 | -120
| 57.7367 | 120 | 57.7367 | 120 | 57.7367 | 120 | 30.6005 | 120
| 0 | 0 | 0.466 | 148 | 3.305 | 132 | 3.8164 | 102
| 0 | 0 | 0 | 0 | 3.305 | 312 | 3.8164 | 342
| 0 | 0 | 0 | 0 | 0 | 210 | 3.8164 | 222
2-Phase | 57.7367 | 150 | 39.1871 | 132.5507
| 57.7367 | 30 | 39.1871 | 47.4493
| 57.7367 | 270 | 57.7367 | 270
| 0 | 0 | 3.305 | 282
| 0 | 0 | 3.305 | 102
| 0 | 0 | 0 | 0
3-Phase | 57.7367 | 0 | 30.6005 | 0
| 57.7367 | -120 | 30.6005 | -120
| 57.7367 | 120 | 30.6005 | 120
| 0 | 0 | 3.8164 | 102
| 0 | 0 | 3.8164 | 342
| 0 | 0 | 3.8164 | 222
Not defined
Trip/Com(Elem))
Parameter
Trip/Com(Sw)
Page 1
Page 2
Page 3
Page 4
Page 8
Page 5
Page 9
Page 7
Page 6
ARC Switch/Element
Page 12
Note on J1: Only used to overlay 'Max Load' circle on Zone Characteristic diagrams. It has no implications for testing.
Note on W1: 30/09/10: Pre release V1.2 02/10/10: DCEF Plots added 20/07/11: Timing test Current Limits changed for 1st test to cope with very short ZR1/long ZR2 combination, AR Deadtime logic changed. Cell formatting changes.
Note on Q2: Relay Connection information only. It has no bearing on relay modelling
Note on AC5: Scaler for nominal current: In 7SA61x, all settings are directly in Ohms, Amps etc. rather than multiples of In. Hence always equal to '1'
Note on G9: Phase Reactive Reach, Zone 1 (Fwd)
Note on J9: Ph-Ph Dir. Blinder Default: 30
Note on M9: Zone 3 Timers, (Fwd)
Note on P9: E/F Reactive Reach, Zone 3 (Fwd)
Note on AB9: Fixed for Toward the Busbar
Note on B10: Forward Resistive Blinder. If set to 'COM(1)', BFRS is common resistive reach is all Fwd Zones. If set to 'IND(2)', BFRS is the resistive blinder for Zone 3. BFR1S, BFR2s etc are the resitive blinders for their respective Zones.
Note on D10: Phase Emergency Overcurrent
Note on G10: Load Compensation Angle, Droop of characteristic (Zone 1, Z1X Phase Characteristic)
Note on J10: Phase Resistive Reach, Zone 3 (Fwd), if 'BLZONE' is set to 'IND(2)' Phase Resistive Reach for all Fwd Zones, if 'BLZONE' is set to 'COM(1)'
Note on M10: Zone R1 Timers, (Rev)
Note on P10: E/F Dir. Blinder Default: 30
Note on B11: If set to '1', TZ1S/TZ1G time delays are bypassed - i.e. all Z1 tripping is instantaneous. 3-pole Definitive Trip for all Z1 faults for Carrier Fail If set to '2', All tripping is 3-phase. TZ1S/TZ1G are bypassed for 'Carrier Fail'. There is no reclosing . Note: Carrier Fail occuring co-incident with the Fault are ignored
Note on D11: E/F Emergency Overcurrent Control to be implemented
Note on G11: Load Compensation Angle, Droop of characteristic (Zone 1, Z1X Phase Characteristic)
Note on J11: Ph-Ph Dir. Blinder Default: 120
Note on M11: Zone R2 Timers, (Rev)
Note on P11: E/F Resistive Reach, Zone 3 (Fwd), if 'BLZONE' is set to 'IND(2)' E/F Resistive Reach for all Fwd Zones, if 'BLZONE' is set to 'COM(1)'
Note on AB11: Toshiba stated 0.08A but test found a min op value of 0.118A
Note on D12: User: For development
Note on G12: Phase Reactive Reach, Zone 1Ext (Fwd)
Note on J12: Phase Reactive Reach, Zone R1 (Rev)
Note on M12: Zone ND, Timers
Note on P12: E/F Dir. Blinder Default: 120
Note on D13: User: For Development
Note on G13: If 'BLZONE' is set to 'IND(2)': Phase Resistive Reach, Zone 1 (Fwd)
Note on J13: Phase Reactive Reach, Zone R2 (Rev)
Note on M13: E/F Reactive Reach, Zone 1 (Fwd)
Note on P13: E/F Reactive Reach, Zone R1 (Rev)
Note on D14: Broken Conductor Tripping. Fixed 'Off'
Note on G14: If 'BLZONE' is set to 'IND(2)': Phase Reactive Reach, Zone 1Ext (Fwd)
Note on J14: Phase Reactive Reach, Zone 4 Blocking of 'Echo' circuit (POTT schemes)
Note on M14: E/F Reactive Reach, Zone 1 Ext (Fwd)
Note on P14: E/F Reactive Reach, Zone R2 (Rev)
Note on V14: Weak Infeed Trip supervision, 3 Phase trip
Note on D15: POTT Zone for Tx/Rx PUTT Zone for Rx
Note on G15: Phase Reactive Reach, Zone 2 (Fwd)
Note on J15: Phase Resistive Reach, Reverse Zones (ZR1, ZR2 and Z4)
Note on M15: Load Compensation Angle, Zone 1 E/F Characteristicc)
Note on P15: E/F Reactive Reach, Zone 4 Blocking of 'Echo' circuit (POTT schemes)
Note on G16: If 'BLZONE' is set to 'IND(2)': Phase Resistive Reach, Zone 2 (Fwd)
Note on J16: Zone ND, Phase Reactive Reach
Note on M16: Load Compensation Angle, Zone 1 E/F Characteristicc)
Note on P16: E/F Resistive Reach, Reverse Zones (ZR1, ZR2 and Z4)
Note on V16: Weak Infeed Trip supervision, 1/3 Phase trip as appropriate
Note on G17: Phase Reactive Reach, Zone 3 (Fwd)
Note on J17: Zone ND, Phase Resistive Reach
Note on M17: If 'BLZONE' is set to 'IND(2)': E/F Resistive Reach, Zone 1 (Fwd)
Note on P17: Resistive Zero-Sequence Compensation Applies to Z1, Z1X load compensation only
Note on B18: Switch 1st Reverse Zone On/Off
Note on D18: Weak Infeed Trip Function
Note on J18: Zone 1 Timers, (Fwd)
Note on M18: If 'BLZONE' is set to 'IND(2)': E/F Resistive Reach, Zone 1 Ext (Fwd)
Note on B19: Switch 2nd Reverse Zone On/Off
Note on J19: Zone 2 Timers, (Fwd)
Note on M19: E/F Reactive Reach, Zone 2 (Fwd)
Note on V19: Forward PU (Carrier Tx) delay
Note on J20: Zone ND, Phase Reactive Reach
Note on M20: If 'BLZONE' is set to 'IND(2)': E/F Resistive Reach, Zone 2 (Fwd)
Note on P20: Reactive Zero-Sequence Compensation
Note on V20: Reverse PU delay Should be set to '0' so that current reversal can operate correctly
Note on J21: Zone ND, Phase Resistive Reach
Note on V21: Transient Block timer (Current reversal)
Note on S23: Minimum Current for Earth Faults
Note on B25: Evolving Fault supervision. Must be set greater than TSPR1
Note on B26: Three-pole Dead-Time
Note on B27: Single Pole Dead Time
Note on B28: Associated with synch check - Generates 3-pole trip and aborts AR cycle if synch conditions are not met, even when synch-check is not employed. For 3-pole only tripping (TPAR): It must be set greater than Dead Time TTPR1 For 1-pole only tripping (SPAR): It must be set greater than Dead Time TSPR1 For 1/3 pole tripping (SPAR&TPAR): It must be set greater than TSPR1 + TTPR1 to cater for evolving faults
Note on C95: Not applicable - Dead Time for multi-phase faults
Note on D102: Standalone Over-Reach for AR when teleprotection is not available

## Characteristic
| Station: | TH |  |  |  | Feeder: | Duns | [26 empty] | OK |  | Timing Delta Current | 3% |  |  | Z1 | Z1x | Z2 | Z3 | ZR1 | ZR2 | Z4(echo Block) | ZND |  | ZE1 | ZE1B | ZE2 | ZE3 | ZE4 | ZE5 |  | Z4(echo Block) |  | Fault detection | Z1 effective | Z1B Acceleration | Z1B Non Dir.
Phase to Phase Faults | [5 empty] | K Factor: | 1 | [26 empty] | Timing Warnings | OK | OK |  |  | Corner Angle | 25.8702 | 35.6903 | 28.0563 | 32.8285 | 209.7529 | 240.4655 | 238.6239 | 55.9732 |  | 11.9483 | 25.6219 | 10.9299 | 18.8594 | 206.265 | 233.5464 |  | 230.7767 |  | 125 | 0 | 0 | 0
[27 empty] | Ph-Ph Plot Data |  |  |  | Ph-E Plot Data |  |  | R-S | Faulty Ph1 | Faulty Ph2 | Healthy Ph | TRUE | Corner Mag | 34.744 | 32.019 | 44.9463 | 71.9389 | 21.7628 | 61.582 | 54.8158 | 106.6633 |  | 70.5415 | 41.6138 | 107.4051 | 116.3196 | 29.1705 | 59.9499 |  | 53.4409 |  | 180 | 18.6714 | 26 | 26
|  | Z1S, Forward |  |  | Z1X, Off |  |  | Z2S, Forward |  |  | Z3S, Forward |  | ZR1S, Reverse |  | ZR2S, Reverse |  | Zone ND |  | Z4 |  | PTT Rx | POTT, Z2 | SOTF | OCH |  |  | R | X |  |  | R | X |  | S-T | Healthy Ph | Faulty Ph1 | Faulty Ph2 | FALSE | b | 10.5712 | 11.342 | 14.3993 | 24.8703 | 7.2023 | 13.4891 | 13.2056 | 28.7407 |  | 10.1259 | 12.578 | 13.7962 | 27.3278 | 8.9662 | 17.5276 |  | 17.5276 |  | 199.8353 | 36.0321 | 46 | 46 |  |  |  | 1 |  |  | X
VA |  | 38.8508 | 312.0075 |  | 56.0368 | 211.0087 |  | 62.1159 | 207.6941 |  | 62.1159 | 207.6941 | 43.5778 | 318.5125 | 29.3204 | 259.9264 | 62.1159 | 207.6941 | 30.508 | 251.1302 | 62.1159 | 207.6941 | 30.8647 | 249.2799 |  | Zone 1 | 24.1789 | -11.2748 |  | Zone 1 | 57.8694 | -26.9849 |  | T-R | Faulty Ph2 | Healthy Ph | Faulty Ph1 | FALSE | c | 25.0617 | 17.6737 | 30.8003 | 43.3759 | 14.2873 | 8.6049 | 9.034 | 21.6788 |  | 64.3077 | 30.1842 | 99.0438 | 96.1935 | 20.8542 | 14.4248 |  | 14.4248 |  | 229.8353 | 90 | 90 | 90 | 24.1789 | -11.2748 | 57.8694 | -26.9849
VB |  | 38.8508 | 227.9925 |  | 57.7367 | 90 |  | 57.7367 | 90 |  | 57.7367 | 90 | 43.5778 | 221.4875 | 57.7367 | 90 | 57.7367 | 90 | 57.7367 | 90 | 57.7367 | 90 | 57.7367 | 90 |  | -12.5 | 25.6748 | -5.692 |  | -12.5 | 61.4497 | -13.6231 |  | Test Voltages /Angles |  |  |  | R-S | d | 8.2206 | 12.4605 | 12.1066 | 24.7219 | 6.429 | 42.6922 | 37.5493 | 71.0402 |  | 4.4974 | 9.694 | 5.8362 | 16.3291 | 7.0722 | 38.5435 |  | 38.5435 |  | 270 | 143.9679 | 134 | 134 | 25.6748 | -5.692 | 61.4497 | -13.6231 | [5 empty] | d
VC |  | 57.7367 | 90 |  | 56.0368 | 328.9913 |  | 62.1159 | 332.3059 |  | 62.1159 | 332.3059 | 57.7367 | 90 | 29.3204 | 280.0736 | 62.1159 | 332.3059 | 30.508 | 288.8698 | 62.1159 | 332.3059 | 30.8647 | 290.7201 |  | 0 | 27.2 | 0 |  | 0 | 65.1 | 0 |  | Phase - Phase |  | Phase - Earth |  |  | Mag | 33.2823 | 30.1341 | 42.9069 | 68.0978 | 20.7163 | 51.2972 | 46.5833 | 92.719 |  | 68.8051 | 39.8782 | 104.88 | 112.5226 | 27.9264 | 52.9682 |  | 52.9682 |  | 297.5 | 161.3286 | 154 | 154 | 27.2 | 0 | 65.1 | 0
Current Limit: [A] |  |  | 3.7731 |  |  | 5.7 |  |  | 5.7237 |  |  | 3.1026 |  | 6.6497 |  | 0.70517 |  | 3.3611 |  | 7.8218 |  | 5.7237 |  | 1.5847 |  | 10.036 | 28.554 | 5.0533 |  | 5 | 66.6627 | 5.8322 |  | Zone 4 | Zone 5 |  |  |  | Corner 2Ang | -33.2329 | -49.4283 | -36.7251 | -44.5988 | 140.5101 | 91.7567 | 94.2283 | 97.9297 |  | -13.4243 | -32.8418 | -12.1559 | -22.6911 | 146.1428 | 101.4646 |  | 105.6614 |  | 125 | 180 | 180 | 180 | 28.554 | 5.0533 | 66.6627 | 5.8322 |  |  |  | c | b
Pulse Duration (Cycles) |  |  | 5 |  |  | 5 |  |  | 25 |  |  | 230 |  | 30 |  | 60 |  | 505 |  |  |  | 5 |  | 5 |  | 18.6714 | 29.9081 | 10.1067 |  | 10 | 68.3283 | 12.0481 |  | 48.5125 | 10.0736 |  |  |  | Corner 2 Mag | 27.662 | 24.5921 | 35.3526 | 55.5446 | 16.9827 | 53.6052 | 46.9277 | 89.2534 |  | 62.9056 | 33.1816 | 96.7117 | 97.4694 | 23.1701 | 49.2017 |  | 42.9963 |  | 180 | 198.6714 | 206 | 206 | 29.9081 | 10.1067 | 68.3283 | 12.0481 | [5 empty] | Slope
ProTest Volts (Fault V) |  |  | 52 |  |  | 96.0571 |  |  | 110 |  |  | 110 |  | 65.2883 |  | 10.2571 |  | 110 |  | 19.7337 |  | 110 | 21 | 21.84 |  | 25.8702 | 31.2621 | 15.16 |  | 11.9237 | 69.0044 | 14.5713 |  | Zone1 | Zone2 |  |  |  | x | 3.9611 | 10.1702 | 7.1842 | 18.6315 | 4.5413 | 29.3861 | 40.953 | 39.262 |  | 12.6228 | 4.5272 | 21.4989 | 3.9268 | 8.3573 | 19.647 |  | 19.647 |  | 220.3103 | 216.0321 | 226 | 226 | 31.2621 | 15.16 | 69.0044 | 14.5713 |  |  |  | a | R
Max. Reach @ Fault V |  |  | 433.3333 |  |  | 800.4755 |  |  | 916.6667 |  |  | 916.6667 |  | 544.0689 |  | 85.4755 |  | 916.6667 |  | 916.6667 |  | 916.6667 |  | 182 |  | 36.0321 | 20.8414 | 15.16 |  | 17.6126 | 46.0029 | 14.6041 |  | 42.0075 | 62.3059 |  |  |  | y | 27.3769 | 22.3906 | 34.6149 | 52.3266 | 16.3642 | 44.8327 | 22.9143 | 80.1541 |  | 61.6261 | 32.8713 | 94.2918 | 97.3903 | 21.6104 | 45.1088 |  | 45.1088 |  | 250.3103 | 270 | 270 | 270 | 20.8414 | 15.16 | 46.0029 | 14.6041
|  | Ang | Imp |  | Ang | Imp |  | Ang | Imp |  | Ang | Imp | Angle | Imped. | Angle | Imped. | Angle | Imped. |  |  | Ang | Imp | Ang | Imp | I | 55.4961 | 10.4207 | 15.16 |  | 32.4124 | 23.0015 | 14.6041 |  | Zone3 | Zone1B |  |  |  | z | -0.69845 | -1.7933 | -1.2668 | -3.2852 | -3.8106 | -24.6579 | -7.2211 | -34.0977 |  | -2.2257 | -0.79827 | -3.7908 | -0.6924 | -7.0126 | -16.4858 |  | -16.4858 |  | 270 | 323.9679 | 314 | 314 | 10.4207 | 15.16 | 23.0015 | 14.6041 |  |  |  | y | z
|  | -25 | 26.6785 |  | -25 | 20.5974 |  | -25 | 33.3481 |  | -25 | 49.0413 | 125 | 18.5069 | 125 | 18.5069 | -55.9732 | 106.6633 | 155 | 15.6932 | -25 | 33.3481 | -25 | 26.6785 | 0.81864 | 90 | 9.2866e-16 | 15.16 |  | 90 | 8.9461e-16 | 14.6041 |  | 62.3059 | 58.9913 |  |  |  | Blinder Mag | 26.6785 | 20.5974 | 33.3481 | 49.0413 | 12.5536 | 20.1748 | 15.6932 | 46.0564 |  | 59.4003 | 32.073 | 90.501 | 96.6979 | 14.5978 | 28.623 |  | 28.623 |  | 290.6087 | 341.3286 | 334 | 334 | 9.2866e-16 | 15.16 | 8.9461e-16 | 14.6041
|  | -12.5 | 26.2982 |  | -12.5 | 20.3038 |  | -12.5 | 32.8728 |  | -12.5 | 48.3423 | 128.219 | 19.2961 | 128.219 | 19.2961 | 0 | 36 | 167.5 | 15.4695 | -12.5 | 32.8728 | 0 | 27.2 | 0.80294 | 102.5 | -3.3609 | 15.16 |  | 102.5 | -3.2377 | 14.6041 |  | Zone6 (Z4) | [23 empty] | 18.5069 | 27.2 | 21 | 21 | -3.3609 | 15.16 | -3.2377 | 14.6041 |  |  |  |  | x
|  | 0 | 27.2 |  | 0 | 21 |  | 0 | 34 |  | 0 | 50 | 180 | 16 | 180 | 16 |  |  | 180 | 16 | 0 | 34 | 18.6714 | 31.5696 | 0.69181 | 115 | -7.0692 | 15.16 |  | 115 | -6.81 | 14.6041 |  | 18.8698 | [23 empty] | 16 | 31.5696 | 26.8771 | 26.8771 | -7.0692 | 15.16 | -6.81 | 14.6041
|  | 10.036 | 28.9977 |  | 13 | 22.9736 |  | 9.3521 | 36.0488 |  | 10.9428 | 53.7084 | 189.9176 | 17.0411 | 200.1552 | 18.9028 | 55.9732 | 106.6633 | 199.5413 | 18.7623 | 9.3521 | 36.0488 | 25.8702 | 34.744 | 0.6286 | Zone 1X | 0 | 0 |  | Zone 1X | 0 | 0 | [6 empty] | m | 5.7476 | 4.4375 | 7.1845 | 10.5655 | 6.5532 | 5.2713 | 3.3809 |  |  | 27.5124 | 13.8196 | 42.2618 | 42.2618 | 18.5948 | 14.9574 |  | 14.9574 |  | 18.829 | 25.7719 | 25.9683 | 25.9683 | 0 | 0 | #REF! | #REF!
|  | 18.6714 | 31.5696 |  | 26 | 26.8771 |  | 18.7042 | 39.477 |  | 21.8857 | 60.3828 | 199.8353 | 18.829 | 220.3103 | 27.1551 |  |  | 219.0826 | 26.3456 | 18.7042 | 39.477 | 90 | 15.16 | 1.4406 | -12.5 | 0 | 0 |  | -25 | 0 | 0 |  | Z2G/ Z3G Overlap | OK |  |  |  | n | 12.3258 | 9.5162 | 15.4072 | 22.6577 | 4.5886 | 6.0177 | 7.2505 |  |  | 59.0006 | 29.6363 | 90.6308 | 90.6308 | 13.0202 | 17.0753 |  | 17.0753 |  | 14.1326 | 15.16 | 18.68 | 18.68 | 0 | 0 | #REF! | #REF!
PCB:1.615A @Vh |  | 25.8702 | 34.744 |  | 35.6903 | 32.019 |  | 28.0563 | 44.9463 |  | 32.8285 | 71.9389 | 209.7529 | 21.7628 | 240.4655 | 61.582 | 90 | 88.4 | 238.6239 | 54.8158 | 28.0563 | 44.9463 | 115 | 16.7272 | 1.3057 | 0 | 0 | 0 |  | -25 | 0 | 0 | [6 empty] | o | 14.6893 | 11.341 | 18.3616 | 27.0024 | 1.6701 | 4.0259 | 8.6408 |  |  | 70.3142 | 35.3191 | 108.0096 | 108.0096 | 4.739 | 11.4234 |  | 11.4234 |  | 10.8 | 25.7719 | 25.9683 | 25.9683 | 0 | 0 | #REF! | #REF!
|  | 36.0321 | 25.7719 |  | 46 | 25.9683 |  | 48.7042 | 28.1374 |  | 51.8857 | 49.5691 | 229.8353 | 14.1326 | 250.3103 | 56.9073 | 124.0268 | 106.6633 | 249.0826 | 50.1019 | 48.7042 | 28.1374 | 125 | 7.28 | 3 | 13 | 0 | 0 |  | -25 | 0 | 0 | [6 empty] | Mag | 20.4369 | 15.7785 | 25.5461 | 37.5678 | 8.2233 | 9.2972 | 12.0217 |  |  | 97.8267 | 49.1387 | 150.2714 | 150.2714 | 23.3337 | 26.3808 |  | 26.3808 |  | 12.1757 | 31.5696 | 26.8771 | 26.8771 | 0 | 0 | #REF! | #REF! | x | 19.647
|  | 55.4961 | 18.3961 |  | 68 | 20.147 |  | 69.3521 | 22.5911 |  | 70.9428 | 41.2614 | 249.9176 | 11.4991 | 260.1552 | 54.3808 | 180 | 36 | 259.5413 | 47.5907 | 69.3521 | 22.5911 | 128.219 | 7.28 | 3 | 26 | 0 | 0 |  | -25 | 0 | 0 |  |  | 48.5125 | [21 empty] | 20 | 18.5069 | 27.2 | 21 | 21 | 0 | 0 | #REF! | #REF! | y | 45.1088
|  | 90 | 15.16 |  | 90 | 18.68 |  | 90 | 21.14 |  | 90 | 39 | 270 | 10.8 | 270 | 53.58 | 235.9732 | 106.6633 | 270 | 46.8 | 90 | 21.14 | 180 | 7.28 | 3 | 35.6903 | 0 | 0 |  | -25 | 0 | 0 |  |  | ZR1 (Z4) |  | ZR2 (Z5) |  | Z1 |  | Z1X |  | Z2 |  | Z3 |  | Fwd Timing |  | PTT |  | SOTF |  | ND |  | Z4 (Z6) |  | 21 | 16 | 31.5696 | 26.8771 | 26.8771 | 0 | 0 | #REF! | #REF! | z | -16.4858
|  | 102.5 | 15.5281 |  | 102.5 | 19.1335 |  | 102.5 | 21.6533 |  | 102.5 | 39.9469 | 297.5 | 12.1757 | 290.6087 | 57.2432 | 270 | 88.4 | 282.5 | 47.9363 | 102.5 | 21.6533 | 240.4655 | 7.28 | 3 | 46 | 0 | 0 |  | -25 | 0 | 0 |  | Faulty Ph1 | 43.5778 | 318.5125 | 29.3204 | 280.0736 | 38.8508 | 312.0075 | 56.0368 | 328.9913 | 62.1159 | 332.3059 | 62.1159 | 332.3059 | 30.2046 | 96.6733 | 62.1159 | 332.3059 | 30.8647 | 290.7201 | 62.1159 | 332.3059 | 30.508 | 288.8698 | 22 | 27.1551 | 25.7719 | 25.9683 | 25.9683 | 0 | 0 | #REF! | #REF! |  | 28.623
|  | 115 | 16.7272 |  | 115 | 20.6111 |  | 115 | 23.3254 |  | 115 | 43.0317 | 325 | 18.8292 | 311.2174 | 71.2296 |  |  | 295 | 51.6381 | 115 | 23.3254 | 270 | 7.28 | 3 | 68 | 0 | 0 |  | -25 | 0 | 0 |  | Faulty Ph2 | 43.5778 | 221.4875 | 29.3204 | 259.9264 | 38.8508 | 227.9925 | 56.0368 | 211.0087 | 62.1159 | 207.6941 | 62.1159 | 207.6941 | 30.2046 | 83.3267 | 62.1159 | 207.6941 | 30.8647 | 249.2799 | 62.1159 | 207.6941 | 30.508 | 251.1302 | 23 | 56.9073 | 15.16 | 18.68 | 18.68 | 0 | 0 | #REF! | #REF!
[15 empty] | 325 | 32.7871 | [6 empty] | 290.6087 | 7.28 | 3 | 90 | 0 | 0 |  | -25 | 0 | 0 |  | Healthy Ph | 57.7367 | 90 | 57.7367 | 90 | 57.7367 | 90 | 57.7367 | 90 | 57.7367 | 90 | 57.7367 | 90 | 60 | 270 | 57.7367 | 90 | 57.7367 | 90 | 57.7367 | 90 | 57.7367 | 90 | 24 | 53.58 | 25.7719 | 25.9683 | 25.9683 | 0 | 0 | #REF! | #REF!
Phase to Earth Faults | [5 empty] | K Factor: | 1 | [18 empty] | 102.5 | 0 | 0 |  | -25 | 0 | 0 |  | Selection | R-S |  | T-R |  | R-S |  | T-R |  | T-R |  | T-R |  | R-S |  | S-T |  | R-S |  | T-R |  | T-R |  | 25 | 57.2432 | 31.5696 | 26.8771 | 26.8771 | 0 | 0 | #REF! | #REF!
|  | Z1G, Forward |  |  | Z1X, Off |  |  | Z2G, Forward |  |  | Z3G, Forward |  | ZR1G, Reverse |  | ZR2G, Reverse |  | Zone ND |  | Z4G |  | PTT Rx | POTT, Z2 | SOTF | OCH |  | 115 | 0 | 0 |  | -25 | No Overreach | 0 |  | No Overreach |  | No Overreach | [20 empty] | 26 | 155 | 0 | -25 | -25 | 0 | 0 | #REF! | #REF!
Faulty Phase R, S, T |  |  | 20.31V, 0º |  |  | 63.51V, 0º |  |  | 28.52V, 0º |  |  | 63.51V, 0º |  | 63.51V, 0º |  | 63.51V, 0º |  | 63.51V, 0º |  | 20.79V, 0º |  | 28.52V, 0º |  | 32.9V, 0º |  | Zone 2 | 30.2237 | -14.0935 |  | Zone 2 | 88.8931 | -41.4515 |  | Z1X Released | [22 empty] | 27 | 180 | 10 | -25 | -25 | 30.2237 | -14.0935 | #REF! | #REF!
Healthy Phase S, T, R |  |  | 63.51V, 240º |  |  | 63.51V, 240º |  |  | 63.51V, 240º |  |  | 63.51V, 240º |  | 63.51V, 240º |  | 63.51V, 240º |  | 63.51V, 240º |  | 63.51V, 240º |  | 63.51V, 240º |  | 63.51V, 240º |  | -12.5 | 32.0935 | -7.115 |  | -12.5 | 94.3928 | -20.9264 | [7 empty] | SOTF | [16 empty] | 28 | 204 | 17.6126 | -25 | -25 | 32.0935 | -7.115 | #REF! | #REF!
Healthy Phase T, R, S |  |  | 63.51V, 120º |  |  | 63.51V, 120º |  |  | 63.51V, 120º |  |  | 63.51V, 120º |  | 63.51V, 120º |  | 63.51V, 120º |  | 63.51V, 120º |  | 63.51V, 120º |  | 63.51V, 120º |  | 63.51V, 120º |  | 0 | 34 | 0 |  | 0 | 100 | 0 |  | DCEF Settings | OK |  |  |  |  | 3 | 7.28 | Ph-Ph | 10.9682 | Ph-E | [12 empty] | 29 | 208 | 90 | -25 | -25 | 34 | 0 | #REF! | #REF!
Current Limit: [A] |  |  | 1.5299 |  |  | 2.1782 |  |  | 1.5406 |  |  | 1.858 |  | 5.4119 |  | 3.1831 |  | 1.5354 |  | 1.0419 |  | 1.5406 |  | 3.3A |  | 9.3521 | 35.5696 | 5.858 |  | 4.5 | 102.1542 | 8.0397 | [7 empty] | -25 | 26.6785 | 26.6785 | 63.8518 | [13 empty] | 30 | 270 | 162.3874 | 205 | 205 | 35.5696 | 5.858 | #REF! | #REF!
Pulse Duration (Cycles) |  |  | 5 |  |  | 5 |  |  | 25 |  |  | 230 |  | 30 |  | 60 |  | 505 |  |  |  | 5 |  | 5 |  | 18.7042 | 37.3921 | 12.6596 |  | 9 | 104.432 | 16.5404 |  | SOTF EF Time | Warning |  |  |  |  | 0 | 27.2 | 27.2 | 65.1 | [13 empty] | 31 | #REF! | 170 | 205 | 205 | 37.3921 | 12.6596 | #REF! | #REF!
ProTest Volts (Fault V) |  |  | 20.3115 |  |  | 63.5104 |  |  | 28.5219 |  |  | 63.51 |  | 63.51 |  | 63.51 |  | 63.51 |  | 20.7875 |  | 28.5219 | 81 | 32.9046 |  | 28.0563 | 39.6644 | 21.14 |  | 10.9299 | 105.4567 | 20.3649 |  | Min SOTF Ph | Error |  |  |  |  | 21.8857 | 31.5696 | 31.5696 | 69.3824 | [13 empty] | 32 | 155 | 180 | 155 | 155 | 39.6644 | 21.14 | #REF! | #REF!
Max. Reach @ Fault V |  | 33.8525 | 84.6313 |  |  | 264.6266 |  |  | 118.8414 |  |  | 264.625 |  | 264.625 |  | 264.625 |  | 264.625 |  | 86.6144 |  | 118.8414 |  | 137.1027 |  | 48.7042 | 18.5692 | 21.14 |  | 13 | 88.2099 | 20.3649 |  | Min SOTF EF | Error |  |  |  |  | 32.8285 | 34.744 | 34.744 | 70.5261 | [13 empty] | 33 | 180 | 190 | 155 | 155 | 18.5692 | 21.14 | #REF! | #REF!
|  | Ang | Imp |  | Ang | Imp |  | Ang | Imp |  | Ang | Imp | Angle | Imped. | Angle | Imped. |  |  | Angle | Imped. | Ang | Imp | Ang | Imp | I | 69.3521 | 7.9662 | 21.14 |  | 51.5 | 16.1989 | 20.3649 |  | Test Voltages | Warning |  |  |  |  | 90 | 15.16 | 15.16 | 14.6041 | [13 empty] | 34 | 232 | 197.6126 | 155 | 155 | 7.9662 | 21.14 | #REF! | #REF!
|  | -25 | 63.8518 |  | -25 | 32.073 |  | -25 | 98.0827 |  | -25 | 98.0827 | 155 | 22.2648 | 155 | 22.2648 |  |  | 155 | 22.2648 | -25 | 98.0827 | -25 | 63.8518 | 0.51533 | 90 | 1.295e-15 | 21.14 |  | 90 | 1.2475e-15 | 20.3649 |  | 15.16 | 90 |  |  |  |  | 115 | 16.7272 | 16.7272 | 16.1139 | [13 empty] | 35 | 236 | 270 | 155 | 155 | 1.295e-15 | 21.14 | #REF! | #REF!
|  | -12.5 | 62.9417 |  | -25 | 32.073 |  | -12.5 | 96.6846 |  | -12.5 | 96.6846 | 167.5 | 21.9474 | 167.5 | 21.9474 |  |  | 167.5 | 21.9474 | -12.5 | 96.6846 | 0 | 65.1 | 0.50545 | 102.5 | -4.6866 | 21.14 |  | 102.5 | -4.5148 | 20.3649 |  | 14.6041 | No Test |  |  |  |  | 125 | 18.5069 | 18.5069 | 22.2648 | [13 empty] | 36 | 270 | 342.3874 | 385 | 385 | -4.6866 | 21.14 | #REF! | #REF!
|  | 0 | 65.1 |  | -25 | 32.073 |  | 0 | 100 |  | 0 | 100 | 180 | 22.7 | 180 | 22.7 | 0 | 45.5 | 180 | 22.7 | 0 | 100 | 10 | 69.3824 | 0.47425 | 115 | -9.8577 | 21.14 |  | 115 | -9.4963 | 20.3649 | [7 empty] | 128.219 | 19.2961 | 19.2961 | 22.7 | [13 empty] | 37 | #REF! | 350 | 385 | 385 | -9.8577 | 21.14 | #REF! | #REF!
|  | 5 | 66.9174 |  | -25 | 32.073 |  | 4.5 | 102.4701 |  | 7 | 104.1785 | 192 | 24.6087 | 206 | 29.0529 |  |  | 204.5 | 28.416 | 4.5 | 102.4701 | 11.9237 | 70.5261 | 0.46656 | Zone 3 | 44.4465 | -20.7258 |  | Zone 3 | 88.8931 | -41.4515 |  | PSB | [5 empty] | 180 | 16 | 16 | 56.1166 | [13 empty] | 38 | 22.2648 | 65.1 | 32.073 | 32.073 | 44.4465 | -20.7258 | #REF! | #REF!
|  | 10 | 69.3824 |  | -25 | 32.073 |  | 9 | 105.7337 |  | 14 | 110.4395 | 204 | 28.2142 | 232 | 56.1166 |  |  | 229 | 50.0182 | 9 | 105.7337 | 90 | 14.6041 | 2.2531 | -12.5 | 47.1964 | -10.4632 |  | -12.5 | 94.3928 | -20.9264 |  | Ph-Ph |  | E/F |  |  |  | 240.4655 | 61.582 | 61.582 | 59.9499 | [13 empty] | 39 | 22.7 | 69.3824 | 32.073 | 32.073 | 47.1964 | -10.4632 | #REF! | #REF!
|  | 11.9237 | 70.5261 |  | -25 | 32.073 |  | 10.9299 | 107.4051 |  | 18.8594 | 116.3196 | 206.265 | 29.1705 | 233.5464 | 59.9499 | 90 | 51.5 | 230.7767 | 53.4409 | 10.9299 | 107.4051 | 115 | 16.1139 | 2.042 | 0 | 50 | 0 |  | 0 | 100 | 0 |  | -25 | 68.6579 | -25 | 107.8909 |  |  | 270 | 53.58 | 53.58 | 48.22 | [13 empty] | 40 | 28.2142 | 48.2654 | 32.073 | 32.073 | 50 | 0 | #REF! | #REF!
|  | 17.6126 | 48.2654 |  | -25 | 32.073 |  | 13 | 90.5302 |  | 24 | 92.4431 | 208 | 27.4962 | 236 | 58.1638 |  |  | 233 | 51.8384 | 13 | 90.5302 | 155 | 10.9682 | 3 | 10.9428 | 52.7319 | 10.1955 |  | 7 | 103.4019 | 12.6962 |  | 0 | 70 | 0 | 110 |  |  | 290.6087 | 57.2432 | 57.2432 | 69.853 | [13 empty] | 41 | 27.4962 | 14.6041 | 32.073 | 32.073 | 52.7319 | 10.1955 | #REF! | #REF!
|  | 32.4124 | 27.2461 |  | -25 | 32.073 |  | 51.5 | 26.0218 |  | 57 | 44.8329 | 239 | 15.0597 | 253 | 50.4233 | 180 | 45.5 | 251.5 | 43.656 | 51.5 | 26.0218 | 180 | 10.9682 | 3 | 21.8857 | 56.031 | 22.5081 |  | 14 | 107.159 | 26.7177 |  | 34.5114 | 104.1354 | 21.1946 | 131.6602 | [19 empty] | 42 | 12.9087 | 48.2654 | 32.073 | 32.073 | 56.031 | 22.5081 | #REF! | #REF!
|  | 90 | 14.6041 |  | -25 | 32.073 |  | 90 | 20.3649 |  | 90 | 37.6 | 270 | 12.9087 | 270 | 48.22 |  |  | 270 | 41.4 | 90 | 20.3649 | 232 | 10.9682 | 3 | 32.8285 | 60.45 | 39 |  | 18.8594 | 110.0749 | 37.6 |  | 90 | 59 | 90 | 47.6 | [19 empty] | 43 | #REF! | 69.3824 | 32.073 | 32.073 | 60.45 | 39 | #REF! | #REF!
|  | 102.5 | 14.9587 |  | -25 | 32.073 |  | 102.5 | 20.8593 |  | 102.5 | 38.5129 | 297.5 | 14.553 | 293.1728 | 52.4517 | 270 | 45.5 | 297.5 | 46.6736 | 102.5 | 20.8593 | 233.5464 | 10.9682 | 3 | 51.8857 | 30.5956 | 39 |  | 24 | 84.451 | 37.6 |  | 115 | 65.0993 | 115 | 52.5208 | [19 empty] | 44 | 22.2648 | 65.1 | 32.073 | 32.073 | 30.5956 | 39 | #REF! | #REF!
|  | 115 | 16.1139 |  | -25 | 32.073 |  | 115 | 22.4701 |  | 115 | 41.487 | 325 | 22.5056 | 316.3456 | 69.853 |  |  | 325 | 72.1787 | 115 | 22.4701 | 270 | 10.9682 | 3 | 70.9428 | 13.4723 | 39 |  | 57 | 24.4177 | 37.6 |  | 125 | 45.3934 | 155 | 32.073 | [19 empty] | 45 | 22.7 | 69.3824 | 32.073 | 32.073 | 13.4723 | 39 | #REF! | #REF!
[15 empty] | 325 | 46.5166 | [6 empty] | 316.3456 | 10.9682 | 3 | 90 | 2.389e-15 | 39 |  | 90 | 2.3033e-15 | 37.6 |  | 180 | 36 | 180 | 32.7 | [19 empty] | 46 | 56.1166 | 48.2654 | 32.073 | 32.073 | 2.389e-15 | 39 | #REF! | #REF!
Timing Tests | [25 empty] | 102.5 | -8.6461 | 39 |  | 102.5 | -8.3357 | 37.6 |  | 232.8665 | 92.2944 | 230.3205 | 75.6469 | [19 empty] | 47 | 58.1638 | 14.6041 | 32.073 | 32.073 | -8.6461 | 39 | #REF! | #REF!
[26 empty] | 115 | -18.186 | 39 |  | 115 | -17.5332 | 37.6 |  | 270 | 73.58 | 270 | 58.22 | [19 empty] | 48 | 48.22 | 48.2654 | 32.073 | 32.073 | -18.186 | 39 | #REF! | #REF!
[26 empty] | Zone R1 | -10.6151 | 15.16 | [5 empty] | 311.2174 | 97.8177 | 316.3456 | 84.3393 | [19 empty] | 49 | #REF! | 69.3824 | 32.073 | 32.073 | -10.6151 | 15.16 | #REF! | #REF!
| Forward, [A] 90º |  |  | Time |  |  | Test Current Phase-Angle | [7 empty] | Inverse Time E/F | [11 empty] | -10.6151 | 15.16 |  | Zone R1 | -20.1787 | 9.4095 | [29 empty] | -11.9379 | 15.16 | #REF! | #REF!
|  |  |  | [ms] |  |  |  | Forward: |  | 90 | º |  |  |  | Angle | 0 | [9 empty] | 128.219 | -11.9379 | 15.16 |  | 167.5 | -21.4272 | 4.7503 | [29 empty] | -16 | 1.9602e-15 | #REF! | #REF!
| Zone 1, | 1.1577 | 2.3172 | 28 |  |  |  | Reverse: |  | 270 | º |  |  |  | A / Ph | Time [s] | [9 empty] | 180 | -16 | 1.9602e-15 |  | 180 | -22.7 | 2.7811e-15 | [29 empty] | -16.7864 | -2.935 | #REF! | #REF!
| t1 | 0.48 | 0.95 | 28 | [21 empty] | 189.9176 | -16.7864 | -2.935 |  | 192 | -24.0709 | -5.1164 | [29 empty] | -17.7119 | -6.389 | #REF! | #REF!
| Zone 1X, | [5 empty] | Ph-Ph Fault Voltages | [18 empty] | 199.8353 | -17.7119 | -6.389 |  | 204 | -25.7749 | -11.4757 | 7SA511 AR Logic | [28 empty] | -18.8939 | -10.8 | #REF! | #REF!
| t1x | [24 empty] | 209.7529 | -18.8939 | -10.8 |  | 206.265 | -26.1589 | -12.9087 | Z1B Untestable | TRUE | Ph-Ph SOTF | OK | [25 empty] | -9.1153 | -10.8 | #REF! | #REF!
| Zone 2, | 0.44917 | 0.89906 | 428 | [21 empty] | 229.8353 | -9.1153 | -10.8 |  | 208 | -24.2777 | -12.9087 | Z1/Z1b Timers |  | P-E SOTF | OK | [25 empty] | -3.9485 | -10.8 | #REF! | #REF!
| t2 | 0.34203 | 0.68461 | 428 |  |  | VA | 30.2046 | 96.6733 |  | 30.3851 | 99.1316 | [13 empty] | 249.9176 | -3.9485 | -10.8 |  | 239 | -7.7563 | -12.9087 | Disp.Z1X | Off | [27 empty] | -1.9847e-15 | -10.8 | #REF! | #REF!
| Zone 3, | 0.32182 | 0.64415 | 4528 |  |  | VB | 30.2046 | 83.3267 |  | 30.3851 | 80.8684 | [13 empty] | 270 | -1.9847e-15 | -10.8 |  | 270 | -2.3723e-15 | -12.9087 | Disp.Z1B | No | [27 empty] | 5.6221 | -10.8 | #REF! | #REF!
| t3 | 0.1854 | 0.3708 | 4528 |  |  | VC | 60 | 270 |  | 60 | 270 | [13 empty] | 297.5 | 5.6221 | -10.8 |  | 297.5 | 6.7198 | -12.9087 | Zone 2 | Forward | [27 empty] | 15.424 | -10.8 | #REF! | #REF!
| Zone 4 ??? | [24 empty] | 325 | 15.424 | -10.8 |  | 325 | 18.4355 | -12.9087 | Disp.Z2 | Yes | [27 empty] | -10.6151 | 15.16 | #REF! | #REF!
| t4 | [5 empty] | Phase-Earth Voltages | [19 empty] | 15.424 | -10.8 |  |  | 18.4355 | -12.9087 | 0 | 0 | [27 empty] | -11.9379 | 15.16 | #REF! | #REF!
| No Op | 0.17444 | 0.34889 | [22 empty] | Zone R2 | -10.6151 | 15.16 |  | Zone R2 | -20.1787 | 9.4095 | Disp.Z3 | Forward |  |  |  |  | Inverse Time E/F | [22 empty] | -16 | 1.9602e-15 | #REF! | #REF!
| Fault Voltage | 7.02 | 13.54 | [23 empty] | -10.6151 | 15.16 |  | 167.5 | -21.4272 | 4.7503 | Disp.R1 | Reverse | [5 empty] | Formatting Info | [21 empty] | -17.7452 | -6.5132 | #REF! | #REF!
[7 empty] | VA | 57.7 | -120 |  | 57.7 | -120 | [13 empty] | 128.219 | -11.9379 | 15.16 |  | 180 | -22.7 | 2.7811e-15 | Disp.R2 | Reverse | [5 empty] | 350 | [21 empty] | -20.7072 | -17.5674 | #REF! | #REF!
| Reverse, [A] 270º |  |  | Time |  |  | VB | 57.7 | 120 |  | 57.7 | 120 | [13 empty] | 180 | -16 | 1.9602e-15 |  | 206 | -26.1126 | -12.736 | Disp. ZND | Off | [5 empty] | 700 | [21 empty] | -30.3567 | -53.58 | #REF! | #REF!
|  |  |  | [ms] |  |  | VC | 13.536 | 0 |  | 17.3592 | 0 | [13 empty] | 200.1552 | -17.7452 | -6.5132 |  | 232 | -34.5489 | -44.2205 | Rounding | 2 | [5 empty] | 875 | [21 empty] | -19.1735 | -53.58 | #REF! | #REF!
| Zone R1, | 4.465 | 6 | 528 | [21 empty] | 220.3103 | -20.7072 | -17.5674 |  | 233.5464 | -35.6205 | -48.22 | Rounding E/F | 2 | [5 empty] | 1166.6667 | [21 empty] | -9.2981 | -53.58 | #REF! | #REF!
| tR1 | 0.91979 | 1.3851 | 528 | [21 empty] | 240.4655 | -30.3567 | -53.58 |  | 236 | -32.5248 | -48.22 | [7 empty] | 1750 | [21 empty] | -9.8465e-15 | -53.58 | #REF! | #REF!
| Zone R2, | 0.86543 | 1.3033 | 1128 | [21 empty] | 250.3103 | -19.1735 | -53.58 |  | 253 | -14.7423 | -48.22 | [7 empty] | 3500 | [21 empty] | 20.1487 | -53.58 | #REF! | #REF!
| tR2 | 0.1854 | 0.3708 | 1128 | [21 empty] | 260.1552 | -9.2981 | -53.58 |  | 270 | -8.8615e-15 | -48.22 | 4 | Voltage for Timing Tests | [5 empty] | 4666.6667 | [21 empty] | 46.9344 | -53.58 | #REF! | #REF!
| No Op | 0.17444 | 0.34889 |  |  |  |  | Back-Up Over-Current | [17 empty] | 270 | -9.8465e-15 | -53.58 | 10 | 293.1728 | 20.64 | -48.22 | Spinner Value | 50 | 50 | 50 | 50 | [24 empty] | 0 | 0 | 0 | 0
| Fault Voltage | 9.6444 | 17.3592 | [22 empty] | 290.6087 | 20.1487 | -53.58 |  | 316.3456 | 50.5398 | -48.22 | V Scaler | 1 | 1 | 1 | 1 |  | Ang | Imp Ph-E |  |  | Z1S/BRRS/7.5 Intersects |  |  |  | ZR1S/BRLS_Ang Intersect | [14 empty] | 0 | 0 | 0 | 0
[26 empty] | 311.2174 | 46.9344 | -53.58 |  | 325 | 38.1042 | -26.6808 | Test V, X axis | 7.02 | 13.536 | 9.6444 | 17.3592 |  | 0 |  |  |  | Point 1a | Pt 1/ 7.5 intersect | 30.7379 |  | Res Reach | 11.1177 | 9.4659 | [12 empty] | 0 | 0 | 0 | 0
[26 empty] | 325 | 26.8576 | -18.8059 |  | 10 | 0 | 0 | Test Angle, +/- | 6.6733 |  | 9.1316 |  |  | 90 |  |  |  | Z1 / Slope | 128.219 | 19.2961 |  | Angle | 334.0936 | 347.0468 | [12 empty] | 0 | 0 | 0 | 0
[26 empty] | PTT | 0 | 0 |  | -12.5 | 0 | 0 | Magnitude [V] | 30.2046 |  | 30.3851 |  |  | 180 | [5 empty] | 20.1748 |  | Limit Ang | 325 | 32.7871 | [12 empty] | 0 | 0 | 0 | 0
[26 empty] | -12.5 | 0 | 0 |  | 0 | 0 | 0 | Max Z, X axis. | 39 | 37.6 | 53.58 | 48.22 |  | 270 |  |  |  | Co-ords | -11.9379 | 15.16 |  | ZR2S/BRLS_Ang Intersect | [14 empty] | 0 | 0 | 0 | 0
[26 empty] | 0 | 0 | 0 |  | 4.5 | 0 | 0 | Max Z, R axis. | 50 | 100 | 26.79 | 22.7 | [5 empty] | Corner | 128.219 | 19.2961 |  | Res Reach | 23.4672 | 11.8991 | [12 empty] | 0 | 0 | 0 | 0
[26 empty] | 9.3521 | 0 | 0 |  | 9 | 0 | 0 | Test Ve, R axis |  | 26.4 |  | 5.9928 |  | 1.1*MaxReach | 76.8383 |  |  | Point 1b | 125 | 18.5069 |  | Angle | 311.2174 | 335.6087 | [12 empty] | 0 | 0 | 0 | 0
[26 empty] | 18.7042 | 0 | 0 |  | 10.9299 | 0 | 0 | [10 empty] | Point 1c | BRRS / 7.5 Intersect | 20.1748 |  | Limit Ang | 325 | 32.7871 | [12 empty] | 0 | 0 | 0 | 0
[26 empty] | 28.0563 | 0 | 0 |  | 13 | 0 | 0 | [10 empty] | Z1, Point 1 | 125 | 18.5069 | [16 empty] | 0 | 0 | 0 | 0
[26 empty] | 48.7042 | 0 | 0 |  | 51.5 | 0 | 0 | Z1 Test points | OK | [8 empty] | Co Ords Z1 / 7.5 | -0.27713 | 15.16 | [16 empty] | 0 | 0 | 0 | 0
[26 empty] | 69.3521 | 0 | 0 |  | 90 | 0 | 0 | [10 empty] | Z1 / 7.5 intersect | 91.0473 | 15.1625 |  | ZR1G/BRLG_Ang Intersect | [14 empty] | 0 | 0 | 57.8694 | -26.9849
[26 empty] | 90 | 0 | 0 |  | 102.5 | 0 | 0 | Max Test V for E/F |  | 28.5219 | [7 empty] | 7.5 /R Axis Intersect |  | 12.9904 |  | Res Reach | 30.1528 | 26.284 | [12 empty] | 0 | 0 | 65.1 | 0
[26 empty] | 102.5 | 0 | 0 |  | 115 | 0 | 0 | [12 empty] | 20.9904 |  | Angle | 336.8238 | 348.4119 | [12 empty] | 0 | 0 | 68.3283 | 12.0481
[26 empty] | 115 | 0 | 0 |  | 0 | 0 | 0 | [10 empty] | Blinder length, Axis to 7.5 line |  | 10.8654 |  | Limit Ang | 325 | 46.5166 | [12 empty] | 0 | 0 | 69.0044 | 14.5713
[26 empty] | 0 | 0 | 0 |  |  |  |  | Z2G Overreach | OK | [8 empty] | Slope / 7.5 intersect | -10.3756 | 20.9904 |  | ZR1/Fwd Zone Crash |  | TRUE | [12 empty] | 0 | 0 | 8.9461e-16 | 14.6041
[26 empty] | PTT | 0 | 0 |  |  |  |  | ZR1G Overreach | OK | [9 empty] | 116.3034 | 23.4147 |  | ZR2G/BRLG_Ang Intersect | [14 empty] | 0 | 0 | -9.9406 | 4.6354
[26 empty] | Z4 | -14.2229 | 6.6322 |  | Z4 | 0 | 0 | AR Setting Discrepancy | OK | [8 empty] | MidPt, Slope/7.5 | -13.1878 | 10.4952 |  | Res Reach | 50.5398 | 31.8085
[26 empty] | 167.5 | -15.1028 | 3.3482 |  | 167.5 | 0 | 0 | AR Effective | OK | [9 empty] | 141.4864 | 16.8543 |  | Angle | 316.3456 | 338.1728
[26 empty] | 180 | -16 | 1.9602e-15 |  | 180 | 0 | 0 | AR Mode | TPAR(3) | [8 empty] | ZR2, Point 1 | 125 | 18.5069 |  | Limit Ang | 325 | 46.5166
[26 empty] | 199.5413 | -17.6816 | -6.2757 |  | 204.5 | 0 | 0 | Z1 Time Effective | OK | [8 empty] | ZR1/ZR2, Pt 2 | 128.219 | 19.2961 |  | ZR2/Fwd Zone Crash |  | TRUE
[26 empty] | 219.0826 | -20.4505 | -16.6093 |  | 229 | 0 | 0 | TZ1S/G | 0 | [8 empty] | Z1=7.58, BRRS=8
[26 empty] | 238.6239 | -28.54 | -46.8 |  | 230.7767 | 0 | 0 | DCEF Volts | 1.7 | [12 empty] | ZR1/ZR2 O/Reaching BRLS
[26 empty] | 249.0826 | -17.8875 | -46.8 |  | 233 | 0 | 0 | [14 empty] | ZR1 | 25.555 | 99999
[26 empty] | 259.5413 | -8.639 | -46.8 |  | 251.5 | 0 | 0 | [9 empty] | Faulty Phase | 13.536 | 17.3592 | Starpoint |  | ZR2 | 126.7811 | 1128
[26 empty] | 270 | -8.6005e-15 | -46.8 |  | 270 | 0 | 0 | [9 empty] | Healthy Phase | 57.7 | 57.7 | 0 |  |  | End point | 1128
[26 empty] | 282.5 | 10.3753 | -46.8 |  | 297.5 | 0 | 0 | Load Plot | [7 empty] | R-E | FALSE | 57.7 | 57.7 | -120
[26 empty] | 295 | 21.8232 | -46.8 |  | 325 | 0 | 0 | 0 | 0 | [6 empty] | S-E | FALSE | 57.7 | 57.7 | 120
[26 empty] | SOTF | 0 | 0 |  | SOTF | 57.8694 | -26.9849 | 0.70711 | 0.70711 | [6 empty] | T-E | TRUE | 13.536 | 17.3592 | 0
[26 empty] | 0 | 0 | 0 |  | 0 | 65.1 | 0 | Voltage Plot
[26 empty] | 18.6714 | 0 | 0 |  | 10 | 68.3283 | 12.0481 | #REF! | #REF!
[26 empty] | 25.8702 | 0 | 0 |  | 11.9237 | 69.0044 | 14.5713 | 0 | 0
[26 empty] | 90 | 0 | 0 |  | 90 | 8.9461e-16 | 14.6041 | #REF! | #REF!
[26 empty] | 115 | 0 | 0 |  | 115 | -6.81 | 14.6041 | #REF! | #REF!
[26 empty] | 125 | 0 | 0 |  | 155 | -9.9406 | 4.6354 | 0 | 0
[26 empty] | 128.219 | 0 | 0 |  | 180 | -10.9682 | 1.3438e-15 | Current Plot
[26 empty] | 180 | 0 | 0 |  | 232 | -6.7527 | -8.6431 | #REF! | #REF!
[26 empty] | 240.4655 | 0 | 0 |  | 233.5464 | -6.517 | -8.8222 | 0 | 0
[26 empty] | 270 | 0 | 0 |  | 270 | -2.0157e-15 | -10.9682 | #REF! | #REF!
[26 empty] | 290.6087 | 0 | 0 |  | 316.3456 | 7.9357 | -7.5714 | #REF! | #REF!
[26 empty] | 0 | 0 | 0 |  |  | 10.9682 | 0 | 0 | 0
[26 empty] | 15 | 0 | 0 |  |  | 10.5945 | 2.8388 | Current Lagging by 45 Deg.
[26 empty] | 30 | 0 | 0 |  |  | 9.4988 | 5.4841
[26 empty] | 45 | 0 | 0 |  |  | 7.7557 | 7.7557 | Measurands
[26 empty] | 60 | 0 | 0 |  |  | 5.4841 | 9.4988 | kV | 63.5
[26 empty] | 75 | 0 | 0 |  |  | 2.8388 | 10.5945 | kA | 0.63
[26 empty] | 90 | 0 | 0 |  |  | 6.7188e-16 | 10.9682 | MW | 111.9
[26 empty] | 105 | 0 | 0 |  |  | -2.8388 | 10.5945 | MVAr | 40.7
[26 empty] | 120 | 0 | 0 |  |  | -5.4841 | 9.4988
|  | Phase-Phase | [5 empty] | Phase-Earth | [17 empty] | 135 | 0 | 0 |  |  | -7.7557 | 7.7557
|  | 1.1577 | 28 | 71.4286 | 71.4286 |  |  | 2.3172 | 28 | 71.4286 | 71.4286 | [14 empty] | 150 | 0 | 0 |  |  | -9.4988 | 5.4841
|  | 0.48 | 28 | 71.4286 | 71.4286 |  |  | 0.95 | 28 | 71.4286 | 71.4286 | [14 empty] | 165 | 0 | 0 |  |  | -10.5945 | 2.8388
[26 empty] | 180 | 0 | 0 |  |  | -10.9682 | 1.3438e-15
[26 empty] | 195 | 0 | 0 |  |  | -10.5945 | -2.8388
|  | 0.44917 | 428 | 4.6729 | 4.6729 |  |  | 0.89906 | 428 | 4.6729 | 4.6729 | [14 empty] | 210 | 0 | 0 |  |  | -9.4988 | -5.4841
|  | 0.34203 | 428 | 4.6729 | 4.6729 |  |  | 0.68461 | 428 | 4.6729 | 4.6729 | [14 empty] | 225 | 0 | 0 |  |  | -7.7557 | -7.7557
|  | 0.32182 | 4528 | 1 | 1 |  |  | 0.64415 | 4528 | 1 | 1 | [14 empty] | 240 | 0 | 0 |  |  | -5.4841 | -9.4988
|  | 0.1854 | 4528 | 1 | 1 |  |  | 0.3708 | 4528 | 1 | 1 | [14 empty] | 255 | 0 | 0 |  |  | -2.8388 | -10.5945
[26 empty] | 270 | 0 | 0 |  |  | -2.0157e-15 | -10.9682
[26 empty] | 285 | 0 | 0 |  |  | 2.8388 | -10.5945
|  | 0.17444 | [5 empty] | 0.34889 | [17 empty] | 300 | 0 | 0 |  |  | 5.4841 | -9.4988
|  | Min Op | 0.12 |  |  |  |  | Min Op | 0.24 | [16 empty] | 315 | 0 | 0 |  |  | 7.7557 | -7.7557
|  | Max Fwd I | 1.1577 | Round | 3 |  |  |  | 2.3172 |  | 3 | [14 empty] | 330 | 0 | 0 |  |  | 9.4988 | -5.4841
[26 empty] | 345 | 0 | 0 |  |  | 10.5945 | -2.8388
|  | 4.465 | 528 | 3.7879 | 3.7879 |  |  | 6 | 528 | 3.7879 | 3.7879 | [14 empty] | 360 | 0 | 0 |  |  | 10.9682 | -2.6875e-15
|  | 0.91979 | 528 | 3.7879 | 3.7879 |  |  | 1.3851 | 528 | 3.7879 | 3.7879 | [14 empty] | PSB | 62.2252 | -29.0161 |  | PSB | 0 | 0
|  | 0.86543 | 1128 | 1.773 | 1.773 |  |  | 1.3033 | 1128 | 1.773 | 1.773 | [15 empty] | 70 | 0 |  |  | 0 | 0
|  | 0.1854 | 1128 | 1.773 | 1.773 |  |  | 0.3708 | 1128 | 1.773 | 1.773 | [15 empty] | 85.809 | 59 |  |  | 0 | 0
|  | 0.17444 | [5 empty] | 0.34889 | [18 empty] | 3.6142e-15 | 59 |  |  | 0 | 0
|  | Max Rev I | 4.465 | Round | 3 |  |  |  | 6 |  | 3 | [15 empty] | -27.5122 | 59 |  |  | 0 | 0
[27 empty] | -26.0366 | 37.1841 |  |  | 0 | 0
[27 empty] | -36 | 4.4105e-15 |  |  | 0 | 0
|  | -14 | 4.9552 | 5 | 5 | [21 empty] | -55.7157 | -73.58 |  |  | 0 | 0
|  | -38.5696 | [24 empty] | -1.3522e-14 | -73.58 |  |  | 0 | 0
|  | 0 | 4.808 | 5 | 5 | [21 empty] | 64.4538 | -73.58 |  |  | 0 | 0
|  | 14.5 | 4.9662 | 5 | 5
|  | 29 | 5.4972 | 5 | 5 | [20 empty] | Fwd Blinder 1 | 52.3513 | -30.225 |  | Blinder 1 | 85.7949 | -49.5337
|  | 38.5696 | 6.1495 | 5 | 5 | [21 empty] | 0 | 0 |  |  | -85.7949 | 49.5337
|  | 49 | 5.0801 | 5 | 5 | [20 empty] | Fwd Blinder 2 | -30.225 | 52.3513 |  | Blinder 2 | 0 | 0
|  | 69.5 | 4.0932 | 5 | 5 | [20 empty] | Rev Blinder 1 | 0 | 0 |  |  | -49.5337 | 85.7949
|  | 90 | 3.834 | 5 | 5 | [20 empty] | Scaler | 60.45 | 0 |  | Scaler | 99.0674
|  | 141.4304 | [23 empty] | Non Directional | 0 | 0 |  | Non Directional
|  | 112 | 4.1351 | 5 | 5 | [20 empty] | 0 | 0 | 0
[26 empty] | 55.9732 | 0 | 0
[26 empty] | 90 | 0 | 0
[26 empty] | 124.0268 | 0 | 0
[26 empty] | 180 | 0 | 0
| Emergency O/C | [6 empty] | Inverse Time E. Fault | [17 empty] | 235.9732 | 0 | 0
|  | [A] | [s] |  |  |  |  | [A] | [s] | Tol + | Tol - | [14 empty] | 270 | 0 | 0
| Phase | 15 | 1028 | [23 empty] | 0 | 0
|  | 7.5 | 1028 | [22 empty] | Slope / 7.5 Line | -10.3756 | 20.9904
|  | 3.15 | 1028 | [23 empty] | 118.784 | -53.58
|  | 2.85 | [23 empty] | ZR1 /BRLS Line | 16 | 0
| Earth | 3.3333 | 1028 | [23 empty] | 22.2354 | -10.8
|  | 1.6667 | 1028 | [23 empty] | 15.424 | -10.8
|  | 0.7 | 1028 | [22 empty] | ZR2 /BRLS Line | 16 | 0
|  | 0.63333 | [24 empty] | 46.9344 | -53.58
[27 empty] | 26.8576 | -53.58
[26 empty] | Z1 | 25.8702 | 34.744
[26 empty] | Co-Ords | 31.2621 | 15.16
[26 empty] | Load Compensation |  |  |  | Load Compensation | 3.7798 | 14.6041
[27 empty] | 0 |  |  |  | 69.0044 | 14.5713
| Back-Up O/C | [24 empty] | Co-Ords #4 | 28.554 | 5.0533
|  | [A] | [ms] | Tol + | Tol - | [21 empty] | 10.036 | 28.9977 |  |  | Load Compensation
| Phase | [24 empty] | Co-Ords #5 | 29.9081 | 10.1067 |  |  | Total Line | 15.0854
[27 empty] | 18.6714 | 31.5696 |  |  | Top segment | 0
[26 empty] | Start Slope | 90 | 15.16 |  |  | Bottom segment | 15.0854
[26 empty] | Co-Ords | 9.2866e-16 | 15.16 |  |  | R Co-ord | 69.0044
[26 empty] | Co-Ords | 15.6311 | 15.16 |  |  | X Co-ord | 14.5713
[26 empty] | Mid Pt | 44.1235 | 21.7751 |  | Start | 75.4892 | 15.0854
| Earth | [24 empty] | Co-Ords | 31.2621 | 15.16 |  | Mid Pt | 43.7064 | 21.1359
|  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [20 empty] | Corner | 25.8702 | 34.744 |  | Corner | 11.9237 | 70.5261
[26 empty] | Co-Ords #7 | 20.8414 | 15.16 |  | Max Reach | 0 | 262.5
[27 empty] | 36.0321 | 25.7719
[26 empty] | Co-Ords #8 | 10.4207 | 15.16
[27 empty] | 55.4961 | 18.3961
[26 empty] | Max Reach | 0 | 916.6667
DCEF
119.8037
[21 empty] | 80.1643 | 89.0315 |  |  | Max Load | 0 |  |  | Max Load | 0 |  |  |  | 46.0029 | 14.6041
| TH | Duns | GRZ100, 1A | [17 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 17.6126 | 48.2654
| Measurands | MW:+111.9 | MVAr:+40.7 | [17 empty] | 0 | 0 |  | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 23.0015 | 14.6041
| In | 1 | 2025-05-15 18:40 | [17 empty] | 0 | 0 |  | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 32.4124 | 27.2461
| Tol | 25 | [18 empty] | 0 | 0 |  | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Meas_Ang | 180 | [18 empty] | 0 | 0 |  | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| I_Ang | 90 | Timing Macros | [17 empty] | 0 | 0 |  | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Max_On | 2 | [18 empty] | 0 | 0 |  | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Dir_Delta | 5 | xls V: 25/8/2011 | [17 empty] | 0 | 0 |  | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| I_Jump_Det | 0.1 | Current Jump for Flt Detection | [17 empty] | 0 | 0 |  | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Z1CNT | 1 | [18 empty] | 0 | 0 |  | 135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CBF_Add_On | 7 | ms (Slower contact monitored) | [17 empty] | 0 | 0 |  | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Meas_V | 57.7367 | [18 empty] | 0 | 0 |  | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Vh | 57.7367 | [18 empty] | 0 | 0 |  | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| UVCV | 0.52 | [18 empty] | 0 | 0 |  | 195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| J_PU | 0.12 | Ph PU | [17 empty] | 0 | 0 |  | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Je_PU | 0.24 | E PU | [17 empty] | 0 | 0 |  | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| VfFwd | 7.02 | [18 empty] | 0 | 0 |  | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| VfRev | 9.6444 | [18 empty] | 0 | 0 |  | 255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ve_F | 13.536 | Fwd EF V | [17 empty] | 0 | 0 |  | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ve_R | 17.3592 | Rev EF V | [17 empty] | 0 | 0 |  | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| End_pt | 1128 | Fwd Z O/R | [17 empty] | 0 | 0 |  | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WEI_UV | 40 | UVLG, 1-Ph drop | [17 empty] | 0 | 0 |  | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| UVLS | 70 | Ph-Ph Drop | [17 empty] | 0 | 0 |  | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Echo | On(1) | [18 empty] | 0 | 0 |  | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WKIT | Off(0) | 1 | [17 empty] | 0 | 0 |  | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ZFSe_Flt_V | 63.51 | Fwd E Start Z
| ZFSe_I_Limit | 5.4119
| BFLS | 120
| RBB | 30 | GRZ100xxx Only
| DCEF_I | 0.1
| DEFRI | 0.1
| DCEF_V | 1.7
| DCEFRV | 1.7
| DEF_Ang | 132
| TDEFF | 0 | ms
| TREBK | 100 | ms
| CBF_I | 0.1
| CBF_t1 | 148
| CBF_t2 | 268
| CBF_t3 | 68
| Dead_Time_1 | 0.7
| Dead_Time_3 | 0.7
| FI1 | 1.158 | Z1
| FI2 | 0.48
| FI3 | Off | Z1B
| FI4 | Off
| FI5 | 0.449 | Z2
| FI6 | 0.342
| FI7 | 0.322 | Z3
| FI8 | 0.185
| FI9 | Off
| FI10 | Off
| FI11 | 0.174
| Ft1 | 28
| Ft2 | 28
| Ft3 | Off
| Ft4 | Off
| Ft5 | 428
| Ft6 | 428
| Ft7 | 4528
| Ft8 | 4528
| Ft9 | Off
| Ft10 | Off
| RI1 | 4.465
| RI2 | 0.92
| RI3 | 0.865
| RI4 | 0.185
| RI5 | 0.174
| Rt1 | 528
| Rt2 | 528
| Rt3 | 1128
| Rt4 | 1128
| FIe1 | 2.317
| FIe2 | 0.95
| FIe3 | Off
| FIe4 | Off
| FIe5 | 0.899
| FIe6 | 0.685
| FIe7 | 0.644
| FIe8 | 0.371
| FIe9 | Off
| FIe10 | Off
| FIe11 | 0.349
| Fte_1 | 28
| Fte_2 | 28
| Fte_3 | Off
| Fte_4 | Off
| Fte_5 | 428
| Fte_6 | 428
| Fte_7 | 4528
| Fte_8 | 4528
| Fte_9 | Off
| Fte_10 | Off
| RIe1 | 6
| RIe2 | 1.385
| RIe3 | 1.303
| RIe4 | 0.371
| RIe5 | 0.349
| Rte_1 | 528
| Rte_2 | 528
| Rte_3 | 1128
| Rte_4 | 1128
| FIe1_R | 0.42 | R-Axis Timing
| FIe2_R | 0.27 | (GRZ100xxx only)
| FIe3_R | 0.27
| FIe4_R | 1.2
| Vh_e | 63.51
| Vh_e_Ang | 120
| Rev_Vh_e | 63.5104
| Rev_Vh_e_Ang | 120
| Test_Ve_Fwd_R | 26.4
| EM_I_t | 1028 | 3
| EM_I_1 | 15
| EM_I_2 | 7.5
| EM_I_3 | 3.15
| EM_I_4 | 2.85
| EM_Ie_t | 1028 | 3
| EM_Ie_1 | 3.333
| EM_Ie_2 | 1.667
| EM_Ie_3 | 0.7
| EM_Ie_4 | 0.633
| Inv_Ang | 0
| InvEF_1 | No Test
| InvEF_2 | No Test
| InvEF_3 | No Test
| InvEF_4 | No Test
| InvEF_5 | No Test
| InvEF_6 | No Test
| InvEF_7 | No Test
| InvEF_8 | No Test
| InvEF_t1 | No Test
| InvEF_t2 | No Test
| InvEF_t3 | No Test
| InvEF_t4 | No Test
| InvEF_t5 | No Test
| InvEF_t6 | No Test
| InvEF_t7 | No Test
| Z1_Cycles | 5 | Z1 Plot
| Z1_V | 52
| Z1_Mag | 38.8508
| Z1_Ang | 42.0075
| Z1_I_Lim | 3.7731
| Rnd_Z1 | 3
| Z1_A1 | -25
| Z1_A2 | -12.5
| Z1_A3 | 0
| Z1_A4 | 10.036
| Z1_A5 | 18.6714
| Z1_A6 | 25.8702
| Z1_A7 | 36.0321
| Z1_A8 | 55.4961
| Z1_A9 | 90
| Z1_A10 | 102.5
| Z1_A11 | 115
| Z1_Z1 | 26.6785
| Z1_Z2 | 26.2982
| Z1_Z3 | 27.2
| Z1_Z4 | 28.9977
| Z1_Z5 | 31.5696
| Z1_Z6 | 34.744
| Z1_Z7 | 25.7719
| Z1_Z8 | 18.3961
| Z1_Z9 | 15.16
| Z1_Z10 | 15.5281
| Z1_Z11 | 16.7272
| Z1e_Cycles | 5
| Z1e_V | 20.3115
| Z1e_I_Lim | 1.5299
| Rnd_Z1e | 3
| Z1e_A1 | -25
| Z1e_A2 | -12.5
| Z1e_A3 | 0
| Z1e_A4 | 5
| Z1e_A5 | 10
| Z1e_A6 | 11.9237
| Z1e_A7 | 17.6126
| Z1e_A8 | 32.4124
| Z1e_A9 | 90
| Z1e_A10 | 102.5
| Z1e_A11 | 115
| Z1e_Z1 | 63.8518
| Z1e_Z2 | 62.9417
| Z1e_Z3 | 65.1
| Z1e_Z4 | 66.9174
| Z1e_Z5 | 69.3824
| Z1e_Z6 | 70.5261
| Z1e_Z7 | 48.2654
| Z1e_Z8 | 27.2461
| Z1e_Z9 | 14.6041
| Z1e_Z10 | 14.9587
| Z1e_Z11 | 16.1139
| Z1B_Cycles | 5 | Z1B Plot
| Z1B_V | 96.0571
| Z1B_Mag | 56.0368
| Z1B_Ang | 58.9913
| Z1B_I_Lim | 5.7
| Rnd_Z1B | 3
| Z1B_t | 30 | For AR on GRZ100xxx
| Z1B_A1 | OFF
| Z1B_A2 | OFF
| Z1B_A3 | OFF
| Z1B_A4 | OFF
| Z1B_A5 | OFF
| Z1B_A6 | OFF
| Z1B_A7 | OFF
| Z1B_A8 | OFF
| Z1B_A9 | OFF
| Z1B_A10 | OFF
| Z1B_A11 | OFF
| Z1B_Z1 | 20.5974
| Z1B_Z2 | 20.3038
| Z1B_Z3 | 21
| Z1B_Z4 | 22.9736
| Z1B_Z5 | 26.8771
| Z1B_Z6 | 32.019
| Z1B_Z7 | 25.9683
| Z1B_Z8 | 20.147
| Z1B_Z9 | 18.68
| Z1B_Z10 | 19.1335
| Z1B_Z11 | 20.6111
| Z1Be_Cycles | 5
| Z1Be_V | 63.5104
| Z1Be_I_Lim | 2.1782
| Rnd_Z1Be | 3
| Z1Be_A1 | OFF
| Z1Be_A2 | OFF
| Z1Be_A3 | OFF
| Z1Be_A4 | OFF
| Z1Be_A5 | OFF
| Z1Be_A6 | OFF
| Z1Be_A7 | OFF
| Z1Be_A8 | OFF
| Z1Be_A9 | OFF
| Z1Be_A10 | OFF
| Z1Be_A11 | OFF
| Z1Be_Z1 | 32.073
| Z1Be_Z2 | 32.073
| Z1Be_Z3 | 32.073
| Z1Be_Z4 | 32.073
| Z1Be_Z5 | 32.073
| Z1Be_Z6 | 32.073
| Z1Be_Z7 | 32.073
| Z1Be_Z8 | 32.073
| Z1Be_Z9 | 32.073
| Z1Be_Z10 | 32.073
| Z1Be_Z11 | 32.073
| Z2_Cycles | 25 | Z2 Plot
| Z2_V | 110
| Z2_Mag | 62.1159
| Z2_Ang | 62.3059
| Z2_I_Lim | 5.7237
| Rnd_Z2 | 3
| Z2_A1 | -25
| Z2_A2 | -12.5
| Z2_A3 | 0
| Z2_A4 | 9.3521
| Z2_A5 | 18.7042
| Z2_A6 | 28.0563
| Z2_A7 | 48.7042
| Z2_A8 | 69.3521
| Z2_A9 | 90
| Z2_A10 | 102.5
| Z2_A11 | 115
| Z2_Z1 | 33.3481
| Z2_Z2 | 32.8728
| Z2_Z3 | 34
| Z2_Z4 | 36.0488
| Z2_Z5 | 39.477
| Z2_Z6 | 44.9463
| Z2_Z7 | 28.1374
| Z2_Z8 | 22.5911
| Z2_Z9 | 21.14
| Z2_Z10 | 21.6533
| Z2_Z11 | 23.3254
| Z2e_Cycles | 25
| Z2e_V | 28.5219
| Z2e_I_Lim | 1.5406
| Rnd_Z2e | 3
| Z2e_A1 | -25
| Z2e_A2 | -12.5
| Z2e_A3 | 0
| Z2e_A4 | 4.5
| Z2e_A5 | 9
| Z2e_A6 | 10.9299
| Z2e_A7 | 13
| Z2e_A8 | 51.5
| Z2e_A9 | 90
| Z2e_A10 | 102.5
| Z2e_A11 | 115
| Z2e_Z1 | 98.0827
| Z2e_Z2 | 96.6846
| Z2e_Z3 | 100
| Z2e_Z4 | 102.4701
| Z2e_Z5 | 105.7337
| Z2e_Z6 | 107.4051
| Z2e_Z7 | 90.5302
| Z2e_Z8 | 26.0218
| Z2e_Z9 | 20.3649
| Z2e_Z10 | 20.8593
| Z2e_Z11 | 22.4701
| Z3_Cycles | 230 | Z3 Plot
| Z3_V | 110
| Z3_Mag | 62.1159
| Z3_Ang | 62.3059
| Z3_I_Lim | 3.1026
| Rnd_Z3 | 3
| Z3_A1 | -25
| Z3_A2 | -12.5
| Z3_A3 | 0
| Z3_A4 | 10.9428
| Z3_A5 | 21.8857
| Z3_A6 | 32.8285
| Z3_A7 | 51.8857
| Z3_A8 | 70.9428
| Z3_A9 | 90
| Z3_A10 | 102.5
| Z3_A11 | 115
| Z3_Z1 | 49.0413
| Z3_Z2 | 48.3423
| Z3_Z3 | 50
| Z3_Z4 | 53.7084
| Z3_Z5 | 60.3828
| Z3_Z6 | 71.9389
| Z3_Z7 | 49.5691
| Z3_Z8 | 41.2614
| Z3_Z9 | 39
| Z3_Z10 | 39.9469
| Z3_Z11 | 43.0317
| Z3e_Cycles | 230
| Z3e_V | 63.51
| Z3e_I_Lim | 1.858
| Rnd_Z3e | 3
| Z3e_A1 | -25
| Z3e_A2 | -12.5
| Z3e_A3 | 0
| Z3e_A4 | 7
| Z3e_A5 | 14
| Z3e_A6 | 18.8594
| Z3e_A7 | 24
| Z3e_A8 | 57
| Z3e_A9 | 90
| Z3e_A10 | 102.5
| Z3e_A11 | 115
| Z3e_Z1 | 98.0827
| Z3e_Z2 | 96.6846
| Z3e_Z3 | 100
| Z3e_Z4 | 104.1785
| Z3e_Z5 | 110.4395
| Z3e_Z6 | 116.3196
| Z3e_Z7 | 92.4431
| Z3e_Z8 | 44.8329
| Z3e_Z9 | 37.6
| Z3e_Z10 | 38.5129
| Z3e_Z11 | 41.487
| Z4_Cycles | 30
| ZFS_Flt_V | 65.2883 | Z4
| VFS_Mag | 43.5778 | ZR1S
| VFS_Ang | 48.5125
| ZFS_I_Limit | 6.6497
| Z4_A1 | 125 | ZR1S
| Z4_A2 | 128.219
| Z4_A3 | 180
| Z4_A4 | 189.9176
| Z4_A5 | 199.8353
| Z4_A6 | 209.7529
| Z4_A7 | 229.8353
| Z4_A8 | 249.9176
| Z4_A9 | 270
| Z4_A10 | 297.5
| Z4_A11 | 325
| Z4_A12 | OFF
| Z4_Z1 | 18.5069
| Z4_Z2 | 19.2961
| Z4_Z3 | 16
| Z4_Z4 | 17.0411
| Z4_Z5 | 18.829
| Z4_Z6 | 21.7628
| Z4_Z7 | 14.1326
| Z4_Z8 | 11.4991
| Z4_Z9 | 10.8
| Z4_Z10 | 12.1757
| Z4_Z11 | 18.8292
| Z4_Z12 | OFF
| Z4e_Cycles | 30 | ZR1G
| Z4e_A1 | 155
| Z4e_A2 | 167.5
| Z4e_A3 | 180
| Z4e_A4 | 192
| Z4e_A5 | 204
| Z4e_A6 | 206.265
| Z4e_A7 | 208
| Z4e_A8 | 239
| Z4e_A9 | 270
| Z4e_A10 | 297.5
| Z4e_A11 | 325
| Z4e_A12 | OFF
| Z4e_Z1 | 22.2648
| Z4e_Z2 | 21.9474
| Z4e_Z3 | 22.7
| Z4e_Z4 | 24.6087
| Z4e_Z5 | 28.2142
| Z4e_Z6 | 29.1705
| Z4e_Z7 | 27.4962
| Z4e_Z8 | 15.0597
| Z4e_Z9 | 12.9087
| Z4e_Z10 | 14.553
| Z4e_Z11 | 22.5056
| Z4e_Z12 | OFF
| Z5_Cycles | 60
| VRS_Mag | 29.3204 | ZR2S
| VRS_Ang | 10.0736
| Z5_A1 | 125 | ZR2S
| Z5_A2 | 128.219
| Z5_A3 | 180
| Z5_A4 | 200.1552
| Z5_A5 | 220.3103
| Z5_A6 | 240.4655
| Z5_A7 | 250.3103
| Z5_A8 | 260.1552
| Z5_A9 | 270
| Z5_A10 | 290.6087
| Z5_A11 | 311.2174
| Z5_A12 | 325
| Z5_Z1 | 18.5069
| Z5_Z2 | 19.2961
| Z5_Z3 | 16
| Z5_Z4 | 18.9028
| Z5_Z5 | 27.1551
| Z5_Z6 | 61.582
| Z5_Z7 | 56.9073
| Z5_Z8 | 54.3808
| Z5_Z9 | 53.58
| Z5_Z10 | 57.2432
| Z5_Z11 | 71.2296
| Z5_Z12 | 32.7871
| Z5e_Cycles | 60 | ZR2G
| Z5e_A1 | 155
| Z5e_A2 | 167.5
| Z5e_A3 | 180
| Z5e_A4 | 206
| Z5e_A5 | 232
| Z5e_A6 | 233.5464
| Z5e_A7 | 236
| Z5e_A8 | 253
| Z5e_A9 | 270
| Z5e_A10 | 293.1728
| Z5e_A11 | 316.3456
| Z5e_A12 | 325
| Z5e_Z1 | 22.2648
| Z5e_Z2 | 21.9474
| Z5e_Z3 | 22.7
| Z5e_Z4 | 29.0529
| Z5e_Z5 | 56.1166
| Z5e_Z6 | 59.9499
| Z5e_Z7 | 58.1638
| Z5e_Z8 | 50.4233
| Z5e_Z9 | 48.22
| Z5e_Z10 | 52.4517
| Z5e_Z11 | 69.853
| Z5e_Z12 | 46.5166
| ZFRe_Flt_V | 63.51 | Rev E Start Z
| ZFRe_I_Limit | 3.1831
| Start_V | 7.7155 | Carrier Start
| Start_Ang | 7.6
| Start_Mag | 29.12
| Start_I_Lim | 0.85728
| Start_Z1 | 16
| Start_Z2 | 10.8
| Start_Z3 | 16
| Start_Z4 | 53.58
| StartE_V | 13.8874
| StartE_I_Lim | 1.291 |  |  | 3 POTT
| StartE_Z1 | 22.7
| StartE_Z2 | 12.9087
| StartE_Z3 | 22.7
| StartE_Z4 | 48.22
| PSBSZ | 10
| PSBGZ | 10
| OR_Zone | Z2
| PTT_Tx_Ang | 62.3059
| PTT_Tx_Mag | 62.1159
| PUTT_V | 110
| PUTT_I_Lim | 5.7237
| PUTT_Mag | 62.1159
| PUTT_Ang | 62.3059
| PUTTe_V | 28.5219
| PUTTe_I_Lim | 1.5406
| Rnd_PUTT | 3
| Rnd_PUTTe | 3
| ZPUTT_A1 | -25
| ZPUTT_A2 | -12.5
| ZPUTT_A3 | 0
| ZPUTT_A4 | 9.3521
| ZPUTT_A5 | 18.7042
| ZPUTT_A6 | 28.0563
| ZPUTT_A7 | 48.7042
| ZPUTT_A8 | 69.3521
| ZPUTT_A9 | 90
| ZPUTT_A10 | 102.5
| ZPUTT_A11 | 115
| ZPUTT_Z1 | 33.3481
| ZPUTT_Z2 | 32.8728
| ZPUTT_Z3 | 34
| ZPUTT_Z4 | 36.0488
| ZPUTT_Z5 | 39.477
| ZPUTT_Z6 | 44.9463
| ZPUTT_Z7 | 28.1374
| ZPUTT_Z8 | 22.5911
| ZPUTT_Z9 | 21.14
| ZPUTT_Z10 | 21.6533
| ZPUTT_Z11 | 23.3254
| ZPUTTe_A1 | -25
| ZPUTTe_A2 | -12.5
| ZPUTTe_A3 | 0
| ZPUTTe_A4 | 4.5
| ZPUTTe_A5 | 9
| ZPUTTe_A6 | 10.9299
| ZPUTTe_A7 | 13
| ZPUTTe_A8 | 51.5
| ZPUTTe_A9 | 90
| ZPUTTe_A10 | 102.5
| ZPUTTe_A11 | 115
| ZPUTTe_Z1 | 98.0827
| ZPUTTe_Z2 | 96.6846
| ZPUTTe_Z3 | 100
| ZPUTTe_Z4 | 102.4701
| ZPUTTe_Z5 | 105.7337
| ZPUTTe_Z6 | 107.4051
| ZPUTTe_Z7 | 90.5302
| ZPUTTe_Z8 | 26.0218
| ZPUTTe_Z9 | 20.3649
| ZPUTTe_Z10 | 20.8593
| ZPUTTe_Z11 | 22.4701
| Z6_V | 19.7337
| Z6_V_Mag | 30.508 | PTT Echo Block
| Z6_V_Ang | -41.1302
| Z6_I1_Ang | 110.9174
| Z6_I2_Ang | 90
| Z6_I3_Ang | 65
| Z6_I1_Mag | 0.39387
| Z6_I2_Mag | 0.42166
| Z6_I3_Mag | 0.38215
| Z6e_V_Mag | 20.7875
| Z6e_I1_Ang | 127
| Z6e_I2_Ang | 90
| Z6e_I3_Ang | 35
| Z6e_Z1_Mag | 51.8384
| Z6e_Z2_Mag | 41.4
| Z6e_Z3_Mag | 72.1787
| Z6e_I1_Mag | 0.40101
| Z6e_I2_Mag | 0.50211
| Z6e_I3_Mag | 0.288
| EF_UV1 | 42
| EF_UV2 | 38
| PTT_TX_V | 110 | PTT Tx
| PTT_Tx_I_Limit | 5.7237 | POTT
| PTT_Dir | 0
| PTT_TX_A1 | -25
| PTT_TX_A2 | -12.5
| PTT_TX_A3 | 0
| PTT_TX_A4 | 9.3521
| PTT_TX_A5 | 18.7042
| PTT_TX_A6 | 28.0563
| PTT_TX_A7 | 48.7042
| PTT_TX_A8 | 69.3521
| PTT_TX_A9 | 90
| PTT_TX_A10 | 102.5
| PTT_TX_A11 | 115
| PTT_TX_Z1 | 33.3481
| PTT_TX_Z2 | 32.8728
| PTT_TX_Z3 | 34
| PTT_TX_Z4 | 36.0488
| PTT_TX_Z5 | 39.477
| PTT_TX_Z6 | 44.9463
| PTT_TX_Z7 | 28.1374
| PTT_TX_Z8 | 22.5911
| PTT_TX_Z9 | 21.14
| PTT_TX_Z10 | 21.6533
| PTT_TX_Z11 | 23.3254
| PTTe_TX_V | 28.5219 | PTTe Tx
| PTTe_Tx_I_Limit | 1.5406
| PTTe_TX_A1 | -25
| PTTe_TX_A2 | -12.5
| PTTe_TX_A3 | 0
| PTTe_TX_A4 | 4.5
| PTTe_TX_A5 | 9
| PTTe_TX_A6 | 10.9299
| PTTe_TX_A7 | 13
| PTTe_TX_A8 | 51.5
| PTTe_TX_A9 | 90
| PTTe_TX_A10 | 102.5
| PTTe_TX_A11 | 115
| PTTe_TX_Z1 | 98.0827
| PTTe_TX_Z2 | 96.6846
| PTTe_TX_Z3 | 100
| PTTe_TX_Z4 | 102.4701
| PTTe_TX_Z5 | 105.7337
| PTTe_TX_Z6 | 107.4051
| PTTe_TX_Z7 | 90.5302
| PTTe_TX_Z8 | 26.0218
| PTTe_TX_Z9 | 20.3649
| PTTe_TX_Z10 | 20.8593
| PTTe_TX_Z11 | 22.4701
| ZFR_Flt_V | 10.2571 | Rev Ph Start Z
| ZFR_I_Limit | 0.70517
| OCH | 3
| SOTF_t_Ang | No Test
| SOTF_Cycles | 5
| SOTF_V | 21.84
| SOTF_Mag | 30.8647
| SOTF_Ang | 20.7201
| SOTF_I_Lim | 1.5847
| Rnd_SOTF | 3
| ZSOTF_A1 | -25
| ZSOTF_A2 | 0
| ZSOTF_A3 | 18.6714
| ZSOTF_A4 | 25.8702
| ZSOTF_A5 | 90
| ZSOTF_A6 | 115
| ZSOTF_A7 | 125
| ZSOTF_A8 | 128.219
| ZSOTF_A9 | 180
| ZSOTF_A10 | 240.4655
| ZSOTF_A11 | 270
| ZSOTF_A12 | 290.6087
| ZSOTF_Z1 | 26.6785
| ZSOTF_Z2 | 27.2
| ZSOTF_Z3 | 31.5696
| ZSOTF_Z4 | 34.744
| ZSOTF_Z5 | 15.16
| ZSOTF_Z6 | 16.7272
| ZSOTF_Z7 | 7.28
| ZSOTF_Z8 | 7.28
| ZSOTF_Z9 | 7.28
| ZSOTF_Z10 | 7.28
| ZSOTF_Z11 | 7.28
| ZSOTF_Z12 | 7.28
| SOTFe_V | 32.9046
| SOTFe_I_Lim | 3.3
| Rnd_SOTFe | 3
| ZSOTFe_A1 | -25
| ZSOTFe_A2 | 0
| ZSOTFe_A3 | 10
| ZSOTFe_A4 | 11.9237
| ZSOTFe_A5 | 90
| ZSOTFe_A6 | 115
| ZSOTFe_A7 | 155
| ZSOTFe_A8 | 180
| ZSOTFe_A9 | 232
| ZSOTFe_A10 | 233.5464
| ZSOTFe_A11 | 270
| ZSOTFe_A12 | 316.3456
| ZSOTFe_Z1 | 63.8518
| ZSOTFe_Z2 | 65.1
| ZSOTFe_Z3 | 69.3824
| ZSOTFe_Z4 | 70.5261
| ZSOTFe_Z5 | 14.6041
| ZSOTFe_Z6 | 16.1139
| ZSOTFe_Z7 | 10.9682
| ZSOTFe_Z8 | 10.9682
| ZSOTFe_Z9 | 10.9682
| ZSOTFe_Z10 | 10.9682
| ZSOTFe_Z11 | 10.9682
| ZSOTFe_Z12 | 10.9682
| VfR_Mag | 29.2683
| VfR_Ang | 9.4832
| VfF_Mag | 29.08
| VfF_Ang | 6.9
| Open_Line | 265 | For SOTF
| Gen_Trafo | 0 | For SOTF
Not defined
Not defined
Not defined
Note on D10: Limited to UVCV x Un All other zones limited to 110% of Un
Note on D32: Limited to 95% of UVCV
Note on C61: White Text on Grey Background indicates NO OP because test current is less than setting for Min. Iph>.
Note on D61: White Text on Grey Background indicates NO OP because test current is less than setting for Min. Iph>.
Note on C63: If test currents are too high to time all zones in one macro, reduce the test voltage to test inner Zones.
Note on BD74: Intersect Angle for intersect between Z1S (Zone 1 reactance reach) and BRRS (Reverse Resistive reach)
Note on BD78: Intersect Angle for intersect between Z1S (Zone 1 reactance reach) and BRRS (Reverse Resistive reach)
Note on BD84: Intersect Angle for intersect between Z1S (Zone 1 reactance reach) and BRRS (Reverse Resistive reach)
Note on BD89: Intersect Angle for intersect between Z1S (Zone 1 reactance reach) and BRRS (Reverse Resistive reach)
Note on BE94: 99999 = No Op
Note on BE95: 99999 = No Op